## 1_INTRO
1 | Energy Mapping Process for Daimler Truck North America
Reference Info
Introduction
From ISO 50001: 2018 Annex A, section A.6, Planning

## 2_Energy IN & OUT
2 |  |  | Energy Mapping Process for Daimler Truck North America
[6 empty] | DTNA Site: | [12 empty] | Fill out for each energy type
[5 empty] | Energy Types INTO and OUT OF the Site Boundaries | [13 empty] | Y |  | N
Energy Types INTO the SITE | [7 empty] | Convert to Primary** | [5 empty] | Site Boundary | [13 empty] | **Convert to Primary (if required) | Energy Types OUT of the SITE
|  | Feedstocks (truck/bus fuel) | [27 empty] | Pass Through = unused input energy (e.g. fuel loaded into trucks or buses)
Liquid Propane (LP) fuel
|  |  | Diesel fuel for trucks/buses | [26 empty] | Non Energy Product, e.g. pure water, bricks, cars, paper, cloth, tires, etc.
Other fuels, not consumed on site
| Y | Primary | [27 empty] | Energy Product |  |  | Energy product sold must be considered as a relevant variable in the model
|  | Y | Natural Gas | [27 empty] | Product Sold containing Energy Content, e.g. gasoline, kerosene, etc.
|  |  | Liquid Propane (LP) | [5 empty] | On Site Storage | [21 empty] | Excess Energy greater than the Energy from an Outside Source (by energy type)
|  |  | Diesel (consumed on site) | [6 empty] | Diesel Fuel |  |  |  |  | Office Buildings | [16 empty] | Grid Delivered Electricity |  | An Energy Product is converted to primary energy using the same multiplier as the energy type that was generated or extracted on-site within the facility boundaries
|  |  | Coal | [6 empty] | Fuel Oil |  | Data Centers |  |  |  | HVAC Loads | [15 empty] | Steam
|  |  | Other Fuel Oils | [6 empty] | LP Gas |  |  | Server Load |  |  | Lighting Loads | [5 empty] | Production Buildings/Warehouses | [9 empty] | Hot Water
| Y | Derived | [7 empty] | Other |  |  | Cooling Load | [9 empty] | Forming, Fabrication, Assembly, Machining | [8 empty] | Chilled Water
|  | Y | Grid Delivered Electricity | [19 empty] | Welding, Heat Treatment, Washing, Drying | [8 empty] | Compressed Air
|  |  | Steam | [19 empty] | Coating, Painting, Curing, Lighting, Testing | [6 empty] | Energy Export |  |  | [at FCCC and Portland from regenerative dynos]
|  |  | Hot Water | [20 empty] | Ventilation, Air Handlers, Exhaust | [6 empty] | Energy SENT to the Outside less than or equal to the Energy from an Outside source (by energy type)
|  |  | Chilled Water | [20 empty] | Process Water & Make-up Air Heating | [7 empty] | Grid Delivered Electricity |  | An Energy Export is converted to primary energy using the same multiplier as the energy type that was delivered to the facility boundaries
|  |  | Compressed Air | [6 empty] | Other Buildings | [7 empty] | Facility Buildings/Rooms | [13 empty] | Steam
|  |  | Solar Electricity | [7 empty] | Training Facilities |  | Thermal Storage | [5 empty] | Air Compressors, Boilers, Pumping | [12 empty] | Hot Water
|  |  | Wind Electricity | [7 empty] | Dining Facilities |  |  | Chilled water |  |  |  |  | Chillers & Cooling Towers | [12 empty] | Chilled Water
|  |  | Geothermal Electricity | [7 empty] | Labs, etc. | [7 empty] | HVAC, Wastewater Treatment, etc. | [12 empty] | Compressed Air
|  |  | Solar/Geo Steam | [21 empty] | Other
|  |  | Still Gas | [5 empty] | Primary Energy Sources from | [6 empty] | On Site Generation | [9 empty] | Solar Panels
|  |  | Various Biomass | [5 empty] | INSIDE the boundaries (extraction) | [20 empty] | CHP Residuals (electricity, steam)
|  |  |  | Agriculture Residue (Hog Waste) | [5 empty] | N | Oil well | [19 empty] | Do not drive energy consumption
|  |  |  | Herbaceous Crops | [5 empty] | N | Natural gas well | [19 empty] | Not included in the energy model
|  |  |  | Woody Crops | [5 empty] | N | Biogas from onsite landfill |  |  |  |  | Combined Heat & Power | [6 empty] | Backup Generators
|  |  |  | Forest Residues | [5 empty] | Y | Renewables on site: solar, wind, etc. | [5 empty] | Electricity | [6 empty] | Diesel | [5 empty] | CHP specifically to sell (electricity, steam)
|  |  |  | Wastewater Sludge | [5 empty] | N | Others | [5 empty] | Steam | [6 empty] | Natural Gas | [6 empty] | Considered a generation product
|  |  |  | Food Scraps (RCI*) | [26 empty] | Must be considered for the energy model
|  |  |  | Other Biogas/Biomass/Biofuel |  |  | **Use Conversion Factors and Multipliers, if using primary energy | [12 empty] | Site Boundary | [6 empty] | **Use Conversion Factors and Multipliers, if using primary energy
These items must be included in the energy accounting:
| *RCI = Restaurants, Cafeterias and Institutions | [8 empty] | Energy producing processes
Exothermic reactions, etc.

## 3A_Energy CONSUMED
3A |  |  | Energy Mapping Process for Daimler Truck North America
Reference Info
Energy CONSUMED within the Site Boundaries
Where does all the energy go?
GOAL: Using the input and outputs from Step 1, determine where all the energy goes within the site boundaries
| METHODS: | [13 empty] | Main Gas Utility Meter | [6 empty] | Gas Meter on a Boiler
|  | Natural Gas: | [5 empty] | Therms/DekaTherms/MMBTU
|  |  | Main utility meter | [6 empty] | CUFT
Sub-meters on equipment
Typically much lower number of end users
Typically well known primary users:
Boilers
Hot water
Process heating
The "H" in HVAC
|  | Electricity: | [5 empty] | kWh
TOP DOWN:
Track the electricity from the utility substation to the end electrical user
[5 empty] | Electrical utility feeders and substations | [14 empty] | One-Line Electrical Drawings | [6 empty] | Motors Control Centers (MCCs)
Main utility meter
Site one-line electrical diagram for distribution
Site substations
[6 empty] | Distribution panels | [5 empty] | Arc Flash Studies
Motor control centers
Busess ducts
Breaker Panels
Local Disconnects
Sub-meters on equipment
Permanent
Temporary
[6 empty] | Electrical End Uses: |  |  |  |  | LOTS & LOTS
Motors, typically the largest
Resistance Heating
Lighting
Actuators
Controls
Plug Loads
[6 empty] | Sub-meters on equipment | [7 empty] | Permanent Sub-Metering | [6 empty] | Temporary Sub-Metering | [5 empty] | Busess Ducts
Permanent
Temporary
Single Phase Calculation
Three Phase Calculation
Name plate data
BOTTOM UP:
Motor Nameplate
Air Compressor Nameplate
Chiller Nameplate
RLA - "Running Load Amps" - current drawn during normal operation of electric motor, typically measured in plant operations
FLA - "Full Load Amps" - amount of current drawn when full-load torque and horsepower is reached for the motor, typically determined in a lab environment
The difference is in the fact that for FLA, you are looking at the rating of the MOTOR itself.
For RLA you are looking at how the motor runs relative to a particular load, e.g. a pump, or a fan, etc.
LRA - "Locked Rotor Amps" - current draw when the rotor is locked and not rotating, typically very high and not used for operational calculations
Typical EXAMPLE for Electrical
[13 empty] | Outside |  |  | Inside |  |  | 34% |  | To Motors Control Centers and Busess Ducts
3%
Busess Duct
100%
|  |  | Utility Substation Transformers | [16 empty] | 480 volt Distribution Center |  |  | 5% | [5 empty] | Local Disconnect
100 kV to 12, 470 volts
Three Phase
[5 empty] | kV = kilovolts | [10 empty] | In Plant Step-Down Transformer
12,470 volts to 480 volts
[18 empty] | Three Phase | [7 empty] | Motor Control Center |  |  | 50 hp Motor
[10 empty] | 60,000,000 kWh/year | [15 empty] | 3,000,000 kWh/year |  |  | Electrical End Use
[10 empty] | Total Electricity IN | [8 empty] | 20,400,000 kWh/year
[19 empty] | Distribution Center |  |  |  |  | 1,800,000 kWh/year |  |  |  | 238085.1064 |  | kWh/year
[24 empty] | Busess Duct |  |  |  | 0.3968%
|  | Liquid Propane: | [6 empty] | Gallons | [18 empty] | Based on:
|  |  | Delivery Tickets | [25 empty] | 6,000 hours per year
|  |  | Monthly Invoices | [25 empty] | 0.94 motor efficiency
|  |  | Submeters on processes | [25 empty] | 1.0 load factor
Is some of this pass through?
i.e. used to fuel trucks or buses
|  | Diesel Fuel: | [6 empty] | Gallons
Delivery Tickets
Monthly Invoices
Submeters on processes
Is some of this pass through?
i.e. used to fuel trucks or buses
Others
How delivered?
Units of delivery
Monthly invoices
M
M
M
M
M

## 3B_Process Block Diagrams
3B
SAMPLE ENERGY FLOW BLOCK DIAGRAMS
Reference Info
| Manufacturing Plant Example: Chiller Production | [10 empty] | Manufacturing Plant Example: Facility Equipment | [19 empty] | Manufacturing Plant Example: Facility Equipment
| Process Block Diagram with Energy | [10 empty] | Chiller System Details, Block Diagram | [19 empty] | Boilers and Hot Water System Details, Block Diagram
|  |  | KEY | IN and OUT | Process Step | Energy Loads |  | Energy Source |  | Waste Stream | Facility System |  |  | KEY | Energy Loads |  |  | Energy Source |  |  | Waste Stream |  |  | Facility System |  | Ambient Air |  |  | Hot Water Supply |  |  | KEY |  | Energy Loads |  | Energy Source |  | Process Step |  | Waste Stream |  | Facility System |  | Hot Water Supply |  | Hot Water Return
[5 empty] | City Water |  | Hot Water-Process |  | Test Water |  |  |  | Chilled Water Supply |  |  |  | Chilled Water Return |  |  | Tower Water SUP |  |  |  | Tower Water RET |  |  | City Water |  |  | Hot Water Return |  |  |  |  | Ambient Air |  | Combustion Air |  | Feed Water |  | Steam |  | Condensate Return |  | City Water
Warm Water to Tower
Cool Water from Tower
Hot Liquid
Exp Valve
Hot Vapor
Warm Vapor
[14 empty] | Cold Liquid | [6 empty] | Chilled Water Return
Chilled Water Supply
HW Return
[19 empty] | Hot Water Control Valve | [5 empty] | Chilled Water Control Valve
Return Air
Supply Air
Outside/Relief Air Dampers
Raw Materials-Water Cooled:
Steel Plate & Bar, Copper Tubes, Motors, Castings and Various Other Components
Final Products:
Water Cooled and Air Cooled Chiller Systems
Paint Booth
(air dried)
Packaging
Warehouse and Shipping
Steel Plate
Plasma Cutting
Motors
Electricity
Raw Materials-Air Cooled:
Heat Exchangers, Fans, Compressors, Motors, Enclosures and Various Other Components
Exhaust Fans
Steel Plate
Roll Forming
Vessel Welding
Water Cooled Chiller Test Lab
Copper Tubing Insertion
Compressed Gas & Hydrostatic Pressure Testing
Final Vessel Assembly
Compressor Assembly
Marriage Mount
Paint
Preparation
Compressor Component Machining
Plasma Cutters
Welder Power Supplies
Hydro Pumps
Air Cooled Unit Test Area
Exhaust Fans
Air Cooled Unit Assembly Lines
Hot Water Heaters to Load Air Cooled Chillers
Natural Gas
Test Water to Load Chillers
Chiller Compressor Motors
Compressor and Fan Motors
Used Hydro Water
Used Test Water
Test Pumps
Dirty Paint
Prep Water
Test Lab Water Control System
Electricity
Motors
Electricity
Gas Compressors
Electricity
Electricity
Electricity
Water Cooled Chillers/Cooling Towers
Water Cooled Chillers
Electricity
Compressors
Evaporators
Make Up Water
Electricity
Tower Fans
Condenser Water Pumps
Condensers
Cooling Towers
Electricity
Typical Air Handling Units (AHUs)
Chilled Water Loads:
Air Handling Unit Coils
Test Lab Water Control System
Pre-Filters
Return Air Fans
Electricity
Supply Air Fans
Electricity
Chilled Water Cooling Coil
Chilled Water
Pumps
Electricity
Hot Water Heating Coil
v
v
Flue Gas
Blow Down
Feed Water Pumps
BOILERS:
Building Heating
Process Heating
Test Lab Chiller Loading
Natural Gas
City Water - Makeup
Boilers and Hot Water
v
Electricity
Combustion Air Supply Fan Motors
Combustion Burners
Steam Hot Water Heaters
Feed Water Tank
Deaerating Feed Tank
DFT Pumps
Electricity
Hot Water Distribution Pumps
v
Electricity
Electricity
Hot Water Loads:
Air Handling Unit Coils
Process Hot Water
Test Lab Water Control System

## 3C_Elec Equip Master
3C |  |  | DTNA Site: |  |  |  |  | COLUMN COLOR KEY |  |  |  |  | INFO NEEDED | [13 empty] | I = Intermittent, on and off, as needed, but not a continuous load, when ON, runs at full load | [22 empty] | COLUMN COLOR KEY |  |  |  |  | Pull Down Menu DATA | Sites ("D") | Electrical Phases ("T") | Load Type | Seasonal Load
|  |  |  | Electrical Equipment Master |  |  |  | DATA YOU CAN GET | [16 empty] | Percent Factor |  | L = ON and runs continuously at FULL load during operations of associated manufacturing line | [12 empty] | 0.746 | kW/HP conversion factor | [8 empty] | DATA YOU CAN GET | [5 empty] | Cleveland | 1 | B | YES
[6 empty] | ALL electrical on ONE |  | DECISION NEEDED, then INPUT Values |  |  |  |  | ESTIMATED | [10 empty] | Winter Hours | 40% |  | V = Variable loads, equipment is ON, but ramps up and down depending on plant needs (air compressors, chillers, motors with VFDs) | [12 empty] | 90% | Power Factor | [8 empty] | DECISION NEEDED, then INPUT Values | [5 empty] | FCCC | 3 | I | NO
[8 empty] | CALCULATED with FORMULA | [15 empty] | Summer Hours | 60% |  | B = ON all the time (i.e. base load, servers, lighting, offices, fans, agitators etc.) | [11 empty] | Rarely Used | 100% | Derating for connected amp rating | [8 empty] | CALCULATED with FORMULA | [5 empty] | Gastonia |  | L
[6 empty] | Total Estimated ANNUAL kWh from this table: | 0 | kWh | [18 empty] | DF = Diversity Factor, to account for things like oven heating, hot water heating heat trace tape, etc. (electric resistance heating) | [18 empty] | Must enter value or equation here if Column "T" = 1 | [9 empty] | HQ Fort mills |  | V
[6 empty] | Total actual ANNUAL kWh from Duke Energy invoices: | 32516160 | kWh | [6 empty] | Must enter a ZERO for HP if a non-motor load | [8 empty] | Full Year | Plant Hours | OF | LF = Load factor for the item, when running/operating. If the items runs at full load during operations, then the LF is 100% | [12 empty] | BTUs/kWh | BTUs/kWh |  |  |  |  | For NON-Motor Loads | [9 empty] | HQ Portland
[5 empty] | For the year: | 2019 | [10 empty] | If HP = ZERO the need these three | [5 empty] | PLANT Operational Factor: | 8760 |  | 0% | OF = Operational Factor is for the plant. What percentage of the total time is the plant operating. | [12 empty] | 3412.14 | 3412.14 | 57.08% |  |  |  | Equation is |  |  |  |  | February | August |  |  |  | Mount Holly
[6 empty] | DELTA: | -32516160 | -100% | [8 empty] | NEED |  | NEED | NEED | [6 empty] | SF = Seasonal Factor should be YES for loads impacted by the season and weather conditions such as HVAC, boilers, and chillers, etc. | [12 empty] | CONVERT | [5 empty] | SITUATIONAL |  |  |  |  | Winter | Summer | Winter | Summer |  | Portland
For Sort | [14 empty] | Nameplate Data from Equipment or Info from Electrical One Line Diagram (record all available) | [11 empty] | OPS | SF | TOTAL HRS |  | PLANT | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer |  |  | Supplemental Electrical Information |  |  | Sub-Metering Info: Measured |  |  |  | Measured | Measured | Calculated | Calculated |  | Saltillo
#1 | #2 | #3 | SITE | BUILDING | DEPT. | SYSTEM | AREA | LOCATION | EQUIPMENT | KEY 1 | KEY 2 | ASSET # | DESCRIPTION | QTY | HP | MEFF | RLA | FLA | PHASES | VOLTAGE | P. AMPS | SUB # | DIST # | MCC # | BUSS DUCT # | PANEL # | CODE | YES or NO | FULL YEAR | DF | OF | LF | LF | ∑HRS | ∑HRS | kW | kW | kWh | kWh | MMBTU | MMBTU | Any Additional Comments/Notes | HVAC/Chiller (TONS/Unit) | Lamps/Fixture | Watts/Lamp | Base kW | Metered | Recorded By | Verification | Calibration | kWh | kWh | kWh | kWh |  | Santiago
1 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
2 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
3 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
4 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
5 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
6 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
7 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
8 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
9 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
10 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
11 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
12 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
13 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
14 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
15 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
16 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
17 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
18 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
19 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
20 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
21 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
22 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
23 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
24 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
25 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
26 | [28 empty] | 8760 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0
| INSERT LINES ONLY - DO NOT DRAG DOWN | [25 empty] | INFO Only | INFO Only |  | Changes kW | Changes Hours | Changes kW | Changes kW |  |  |  | TOTALS | 0 | 0 | 0 | 0
[38 empty] | Winter | Summer | Winter | Summer
[38 empty] | kWh | kWh | MMBTU | MMBTU
[39 empty] | 0 |  | 0
0
CHECKS
`
The tables below are created manually by sorting the above lines.
These do not update automatically.
The data from the tables below are used to create Energy USE pie charts.
[38 empty] | DONE | DEPT | SYSTEM | ELEC EQUIV
[30 empty] | kWh: SORT 1; MMBTU: SORT 2; MMBTU: MMBTU | # of Line Items
[30 empty] | kWh: EXAMPLE; kWh: ALL; MMBTU: *, AIR COND, AMU/AHU, CHILL, FAN, FILTER, HEATER, HVAC, PUMP, VENT; MMBTU: 58240.9 | 251 | HVAC
[30 empty] | kWh: ALL; MMBTU: AIRDRYER, COMP, T-CMPRSR; MMBTU: 10037.6 | 40 | COMPRESSED AIR |  | Breakdown of HVAC
[30 empty] | kWh: ALL; MMBTU: MANF - WELD; MMBTU: 21203.5 | 228 |  |  | AIR COND | 4301.5 | 23
[30 empty] | kWh: ALL; MMBTU: MANF EQUIP (24 types); MMBTU: 8795 | 354 |  |  | AMU/AHU | 22259.6 | 77
[30 empty] | kWh: ALL; MMBTU: BOILER; MMBTU: 118.1 | 4 |  |  | CHILL | 7948.9 | 11
[30 empty] | kWh: ALL; MMBTU: LIGHTING; MMBTU: 5518.4 | 27 |  |  | FAN | 6865.4 | 61
[30 empty] | kWh: ALL; MMBTU: BOOTH, OVEN, PAINT (fans); MMBTU: 4887 | 58 |  |  | FILTER FAN | 1598.8 | 17
[30 empty] | MMBTU: TOTALS; MMBTU: 108800.5 | 962 | 962 |  | HEATING Fans | 8452.7 | 6 | MUA Heating FANS
[30 empty] | MMBTU: 108800.5 |  | LINES |  | HEATING | 84.4 | 6 | IR, Hot Water
[30 empty] | MMBTU: CHECKS |  |  |  | HVAC (AC) | 5768 | 27
[45 empty] | PUMPS | 616.4 | 16
[45 empty] | VENT | 144.2 | 3
[30 empty] | kWh: KEY 1; MMBTU: KEY 2; MMBTU: ELEC EQUIV |  |  |  | * | 201 | 4
[30 empty] | kWh: SORT 1; MMBTU: SORT 2; MMBTU: MMBTU | # of Line Items |  |  |  | 58240.9 | 251
[30 empty] | kW: Breakdown of MOTORs; kWh: ELEC; MMBTU: HOT WATER; MMBTU: 37.1 | 2 |  |  |  | CHECKS | CHECKS
[30 empty] | ∑HRS: KEY 1; ∑HRS: KEY 2; kW: ELEC EQUIV; kWh: ELEC; MMBTU: LASER; MMBTU: 147.9 | 3
[34 empty] | SORT 1 | SORT 2 | MMBTU | # of Line Items | MMBTU/Line | ELEC | PLASMA CUT | 1312.4 | 60
[34 empty] | MOTOR | BLOWER | 442.4 | 18 | 24.5778 | ELEC | WELD | 21203.5 | 228
[34 empty] | MOTOR | C. AIR | 10037.6 | 40 | 250.94 | IR HEAT | HVAC | 47.4 | 4
[34 empty] | MOTOR | CHILL, EVAP, HVAC | 36430.6 | 120 | 303.5883 | LIGHT | All Types | 5518.4 | 27
[34 empty] | MOTOR | CONV, MACH, MAT HAND | 6160 | 260 | 23.6923 | ROBOT | WELD & Mat Hand | 1081.2 | 25
[34 empty] | MOTOR | FAN | 22725 | 151 | 150.4967 | MOTOR | All Types | 79452.9 | 613
[34 empty] | MOTOR | PUMP | 3657.8 | 24 | 152.4083
[34 empty] | MOTOR |  |  |  | #DIV/0!
[30 empty] | kW: 79453.4; kW: 613; kWh: 129.614; MMBTU: TOTALS; MMBTU: 108800.8 | 962 | 962
[30 empty] | kW: CHECKS; kWh: Average; MMBTU: 108800.8 |  | LINES
[36 empty] | 0.5 |  |  |  |  | CHECKS
CHECKS
Note on AD9: Author: Default of 365 days times 24 hours per day
Note on AF9: Author: Changing plant OF only changes HOURS, not kW.
Note on AG9: Author: Changing LF will change the calculated kW.
Note on AH9: Author: Changing LF will change the calculated kW.
Note on D10: Author: Pull down menu.
Note on E10: Author: Name or Number
Note on J10: Author: This is the item actually consuming the electricity
Note on P10: Author: Must put in a ZERO for non-motor loads.
Note on Q10: Author: Use nameplate data, if available. Use EPAct Motor Efficiencies, if unknown. Table of EPAct shown on tab 3C1.
Note on R10: Author: RLA - "Running Load Amps" - current drawn during normal operation of electric motor, typically measured in plant operations and is typically lower than FLA.
Note on S10: Michael Stowe: FLA - "Full Load Amps" - amount of current drawn when full-load torque and horsepower is reached for the motor, typically determined in a lab environment. Typically higher than RLA.
Note on V10: Author: For NON Motors. Panel breaker or feeder amps from nameplate or label plate on a particular circuit or control panel.
Note on AE10: Author: Typically, if you have a diversity factor < 100% you will NOT also derate load factor. Only one or the other of DF or LF should be derated. Changing DF will change calculated kW
Note on AF10: Author: This defaults to the value in cell AA7. Enter manually if different.
Note on AG10: Author: Only one or the other of DF or LF should be derated.
Note on AH10: Author: Only one or the other of DF or LF should be derated.

## 3C1_EPAct Motor Eff.
3C1 |  | Nominal Full Load Efficiencies - EPACT Electric Motors | [9 empty] | Reference Info
|  |  | Open Frame |  |  |  | Closed Frame
|  | HP | 2 Pole | 4 Pole | 6 Pole | 8 Pole | 900 | 1200 | 1800 | 3600 | RPM
[7 empty] | R | S | T | U
| 1 | 1 | N/A | 82.5 | 80 | 74 | 74 | 80 | 82.5 | 75.5
| 2 | 1.5 | 82.5 | 84 | 84 | 75.5 | 77 | 85.5 | 84 | 82.5 |  | If you do not have a motor efficiency, use this table for the motor efficiency values for column "Q" on tab 3C.
| 3 | 2 | 84 | 84 | 85.5 | 85.5 | 82.5 | 86.5 | 84 | 84
| 4 | 3 | 84 | 86.5 | 86.5 | 86.5 | 84 | 87.5 | 87.5 | 85.5
| 5 | 5 | 85.5 | 87.5 | 87.5 | 87.5 | 85.5 | 87.5 | 87.5 | 87.5
| 6 | 7.5 | 87.5 | 88.5 | 88.5 | 88.5 | 85.5 | 89.5 | 89.5 | 88.5
| 7 | 10 | 88.5 | 89.5 | 90.2 | 89.5 | 88.5 | 89.5 | 89.5 | 89.5
| 8 | 15 | 89.5 | 91 | 90.2 | 89.5 | 88.5 | 90.2 | 91 | 90.2
| 9 | 20 | 90.2 | 91 | 91 | 90.2 | 89.5 | 90.2 | 91 | 90.2
| 10 | 25 | 91 | 91.7 | 91.7 | 90.2 | 89.5 | 91.7 | 92.4 | 91
| 11 | 30 | 91 | 92.4 | 92.4 | 91 | 91 | 91.7 | 92.4 | 91
| 12 | 40 | 91.7 | 93 | 93 | 91 | 91 | 93 | 93 | 91.7
| 13 | 50 | 92.4 | 93 | 93 | 91.7 | 91.7 | 93 | 93 | 92.4
| 14 | 60 | 93 | 93.6 | 93.6 | 92.4 | 91.7 | 93.6 | 93.6 | 93
| 15 | 75 | 93 | 94.1 | 93.6 | 93.6 | 93 | 93.6 | 94.1 | 93
| 16 | 100 | 93 | 94.1 | 94.1 | 93.6 | 93 | 94.1 | 94.5 | 93.6
| 17 | 125 | 93.6 | 94.5 | 94.1 | 93.6 | 93.6 | 94.1 | 94.5 | 94.5
| 18 | 150 | 93.6 | 95 | 94.5 | 93.6 | 93.6 | 95 | 95 | 94.5
| 19 | 200 | 94.5 | 95 | 94.5 | 93.6 | 94.1 | 95 | 95 | 95
| 20 | 250 | 94.5 | 95.4 | 95.4 | 94.5 | 94.5 | 95 | 95 | 95.4
| 21 | 300 | 95 | 95.4 | 95.4 | N/A | N/A | 95 | 95.4 | 95.4
| 22 | 350 | 95 | 95.4 | 95.4 | N/A | N/A | 95 | 95.4 | 95.4
| 23 | 400 | 95.4 | 95.4 | N/A | N/A | N/A | N/A | 95.4 | 95.4
| 24 | 450 | 95.8 | 95.8 | N/A | N/A | N/A | N/A | 95.4 | 95.4
| 25 | 500 | 95.8 | 95.8 | N/A | N/A | N/A | N/A | 95.8 | 95.4
TYPICAL

## 3D_Combustion Equip Master
3D |  |  | DTNA Site: |  |  |  | INFO NEEDED | COLUMN COLOR KEY |  |  |  |  | COLUMN COLOR KEY | [5 empty] | I = Intermittent, on and off, as needed, but not a continuous load, when ON, runs at full load | [11 empty] | COLUMN COLOR KEY
|  |  |  | Combustion Equipment Master |  |  |  | DATA YOU CAN GET |  |  |  |  | DATA YOU CAN GET |  |  |  | Percent Factor |  | L = ON and runs continuously during operations of associated manufacturing line | [11 empty] | DATA YOU CAN GET
[6 empty] | ALL Natural Gas on ONE |  | DECISION NEEDED, then INPUT Values |  |  |  |  | DECISION NEEDED, then INPUT Values |  |  | Winter Hours | 50% |  | V = Variable loads, equipment is ON, but ramps up and down depending on plant needs (air compressors & chillers) | [11 empty] | DECISION NEEDED, then INPUT Values
[6 empty] | Other Combustion MMBTU from this table: | 0 | CALCULATED with FORMULA |  |  |  |  | CALCULATED with FORMULA |  |  | Summer Hours | 50% |  | B = ON all the time (i.e. base load, servers, lighting, offices, certain fans, safety equipment, etc.) | [11 empty] | CALCULATED with FORMULA
[6 empty] | Total Estimated ANNUAL Natural Gas MMBTU from this table: | 166692.4024 | MMBTU | [10 empty] | DF = Diversity Factor, to account for things like oven heating, hot water heating, etc. (fossil fuel heating)
[6 empty] | Total actual ANNUAL MMBTU from all natural gas invoices: | 162587.0238 | MMBTU |  |  |  |  | ESTIMATED |  |  | Full Year | Plant Hours | OF | LF = Load factor for the item, when running/operating. If the items runs at full load during operations, then the LF is 100%
[5 empty] | For the year: | 2019 | [8 empty] | PLANT Operational Factor: | 8760 | 2128 | 24.29% | OF = Operational Factor for the plant. What percentage of the total time is the plant running. | [15 empty] | February | August
[6 empty] | DELTA: | 4105.3787 | 2.525% | [10 empty] | SF = Seasonal Factor should be YES for loads impacted by the season and weather conditions | [15 empty] | Winter | Summer | Winter | Summer
For Sort | [14 empty] | Nameplate Data from Combustion Burner Equipment |  |  |  | OPS | SF | TOTAL HRS |  | PLANT | Winter | Summer | Winter | Summer | Winter | Summer |  | Sub-Metering Info: Measured |  |  |  | Measured | Measured | Calculated | Calculated
#1 | #2 | #3 | SITE | BUILDING | DEPT. | SYSTEM | AREA | LOCATION | EQUIPMENT | KEY 1 | KEY 2 | ASSET # | DESCRIPTION | QUANTITY | BTU/HR | COMBEFF | Other | Other | CODE | Y/N | FULL YEAR | DF | OF | LF | LF | ∑HRS | ∑HRS | MMBTU | MMBTU | Any Additional Comments | Metered | Recorded By | Verification | Calibration | MMBTU | MMBTU | MMBTU | MMBTU
1 |  |  | Thomas BB | Plt02A | B1 | AMU/AHU |  | P2-S1400 | Air Handler | HVAC | HEAT | AHD09 | Air Handler Unit C2 (Mazzanine Office) | 1 | 860479 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 50% | 0% | 1064 | 1064 | 314.7202 | 0 | [7 empty] | 314.7202 | 0
2 |  |  | Thomas BB | Plt02A | B1 | AMU/AHU |  | P2-S1400 | Air Handler | HVAC | HEAT | AHD08 | Air Handler Unit C2 (Mezzanine Office) | 1 | 860479 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 50% | 0% | 1064 | 1064 | 314.7202 | 0 | [7 empty] | 314.7202 | 0
3 |  |  | Thomas BB | Plt02A | B1 | AMU/AHU |  | P2-S1400 | Air Handler | HVAC | HEAT | AHD07 | Air Handler Unit C2 (Office) | 1 | 860479 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 50% | 0% | 1064 | 1064 | 314.7202 | 0 | [7 empty] | 314.7202 | 0
11 |  |  | Thomas BB | Plt02A | B1 | AMU/AHU |  | P2-S1400 | Air Handler | HVAC | HEAT | AHD19 | Air Handler Unit C2 (Maintenance) | 1 | 860479 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 65% | 0% | 1064 | 1064 | 409.1363 | 0 | [7 empty] | 409.1363 | 0
20 |  |  | Thomas BB | Plt02A | B3 | AMU/AHU | C2 Paint | TBB-S-2A2014000 | Air Handler | HVAC | HEAT | AHD28 | Air MakeUp Unit, Wipe Down (Line 1) | 1 | 7035000 | 80% |  |  | L | YES | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 3714.48 | 696.465 | [7 empty] | 3714.48 | 696.465
21 |  |  | Thomas BB | Plt02A | B3 | AMU/AHU | C2 Paint | TBB-S-2A2003000 |  | HVAC | HEAT | AHD29 | Air MakeUp Unit, Automatic Paint (Line 1) | 1 | 11690000 | 80% |  |  | L | YES | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 6172.32 | 1157.31 | [7 empty] | 6172.32 | 1157.31
22 |  |  | Thomas BB | Plt02A | B3 | AMU/AHU | C2 Paint | TBB-S-2A2003000 |  | HVAC | HEAT | AHD30 | Air MakeUp Unit, Manual Paint (Line 1) | 1 | 7035000 | 80% |  |  | L | YES | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 3714.48 | 696.465 | [7 empty] | 3714.48 | 696.465
23 |  |  | Thomas BB | Plt02A | B3 | PAINT | C2 Paint |  | Gas Burner Oven | OVEN | COMB | OV09 | Convection Oven - Zone 1 | 1 | 2000000 | 80% |  |  | L | NO | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 1056 | 198 | [7 empty] | 1056 | 198
24 |  |  | Thomas BB | Plt02A | B3 | PAINT | C2 Paint |  | Gas Burner Oven | OVEN | COMB | OV09 | Convection Oven - Zone 2 | 1 | 2000000 | 80% |  |  | L | NO | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 1056 | 198 | [7 empty] | 1056 | 198
25 |  |  | Thomas BB | Plt02A | B3 | AMU/AHU | C2 Paint | TBB-S-2A2014000 |  | HVAC | HEAT | AHD32 | Air MakeUp Unit, Wipe Down (Line 2) | 1 | 7035000 | 80% |  |  | L | YES | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 3714.48 | 696.465 | [7 empty] | 3714.48 | 696.465
26 |  |  | Thomas BB | Plt02A | B3 | AMU/AHU | C2 Paint | TBB-S-2A2004000 |  | HVAC | HEAT | AHD33 | Air MakeUp Unit, Manual Paint (Line 2) | 1 | 11690000 | 80% |  |  | L | YES | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 6172.32 | 1157.31 | [7 empty] | 6172.32 | 1157.31
27 |  |  | Thomas BB | Plt02A | B3 | AMU/AHU | C2 Paint | TBB-S-2A2016000 |  | HVAC | HEAT | AHD34 | Air MakeUp Unit, De-Mask Booth (Line 2) | 1 | 7035000 | 80% |  |  | L | YES | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 3714.48 | 696.465 | [7 empty] | 3714.48 | 696.465
28 |  |  | Thomas BB | Plt02A | B3 | PAINT | C2 Paint |  | Gas Burner Oven | OVEN | COMB | OV10 | Infrared/Convection Oven | 1 | 13456000 | 80% |  |  | L | NO | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 7104.768 | 1332.144 | [7 empty] | 7104.768 | 1332.144
29 |  |  | Thomas BB | Plt02A | B3 | AMU/AHU | C2 Paint |  |  | HVAC | HEAT | AHD36 | Air MakeUp Unit, Sanding Booth | 1 | 7035000 | 80% |  |  | L | YES | 1920 | 55% | 100% | 80% | 15% | 960 | 960 | 3714.48 | 696.465 | [7 empty] | 3714.48 | 696.465
30 |  |  | Thomas BB | Plt02B | 30 | AMU/AHU |  | AHD06 |  | HVAC | HEAT |  | Air MakeUp Unit, Heated, 120,000 CFM | 1 | 8580000 | 80% |  |  | V | YES | 1920 | 55% | 24.29% | 100% | 0% | 233.2055 | 233.2055 | 1375.6208 | 0 | [7 empty] | 1375.6208 | 0
31 |  |  | Thomas BB | Plt09 |  | HVAC |  |  |  | HVAC | HEAT | AHD45 | Air Handling Unit (Plant 9) | 1 | 4000000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 80% | 0% | 1064 | 1064 | 2340.8 | 0 | [7 empty] | 2340.8 | 0
32 |  |  | Thomas BB | Plt09 |  | HVAC |  |  |  | HVAC | HEAT | AHD46 | Air Handling Unit (Plant 9) | 1 | 4000000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 80% | 0% | 1064 | 1064 | 2340.8 | 0 | [7 empty] | 2340.8 | 0
33 |  |  | Thomas BB | Plt01 | 14 | AMU/AHU |  |  |  | HVAC | HEAT | AHD37 | Air Handler, Heated (Plt01 Paint Booth) | 1 | 7035000 | 80% |  |  | V | YES | 1920 | 55% | 50% | 60% | 15% | 480 | 480 | 1392.93 | 348.2325 | [7 empty] | 1392.93 | 348.2325
34 |  |  | Thomas BB | Plt01 | 14 | AMU/AHU |  |  |  | HVAC | HEAT | AHD38 | Air Handler, Heated (Plt01 Paint Booth) | 1 | 7035000 | 80% |  |  | V | YES | 1920 | 55% | 50% | 60% | 15% | 480 | 480 | 1392.93 | 348.2325 | [7 empty] | 1392.93 | 348.2325
35 |  |  | Thomas BB | Plt01 | 14 | AMU/AHU |  |  |  | HVAC | HEAT | AHD39 | Air Handler, Heated (Plt01 Paint Booth) | 1 | 7035000 | 80% |  |  | V | YES | 1920 | 55% | 50% | 60% | 15% | 480 | 480 | 1392.93 | 348.2325 | [7 empty] | 1392.93 | 348.2325
36 |  |  | Thomas BB | Plt01 | 14 | AMU/AHU |  |  |  | HVAC | HEAT | AHD40 | Air Handler, Heated (Plt01 Paint Booth) | 1 | 7035000 | 80% |  |  | V | YES | 1920 | 55% | 50% | 60% | 15% | 480 | 480 | 1392.93 | 348.2325 | [7 empty] | 1392.93 | 348.2325
37 |  |  | Thomas BB | Plt01 | 92 | AMU/AHU |  |  |  | HVAC | HEAT | AHD41 | Air Handler, Heated (Plt01 Paint Booth Minotour) | 1 | 7035000 | 80% |  |  | V | YES | 1920 | 55% | 50% | 60% | 15% | 480 | 480 | 1392.93 | 348.2325 | [7 empty] | 1392.93 | 348.2325
38 |  |  | Thomas BB | Plt01 | 92 | AMU/AHU |  |  |  | HVAC | HEAT | AHD42 | Air Handler, Heated (Plt01 Paint Booth Minotour) | 1 | 7035000 | 80% |  |  | V | YES | 1920 | 55% | 50% | 60% | 15% | 480 | 480 | 1392.93 | 348.2325 | [7 empty] | 1392.93 | 348.2325
39 |  |  | Thomas BB | Plt01 | 92 | AMU/AHU |  |  |  | HVAC | HEAT | AHD43 | Air Handler, Heated (Plt01 Paint Booth Minotour) | 1 | 7035000 | 80% |  |  | V | YES | 1920 | 55% | 50% | 60% | 15% | 480 | 480 | 1392.93 | 348.2325 | [7 empty] | 1392.93 | 348.2325
40 |  |  | Thomas BB | Plt01 | 14 | AMU/AHU |  |  |  | HVAC | HEAT | AHD44 | Air Handler, Heated (Plt01 Paint Booth Minotour) | 1 | 7035000 | 80% |  |  | V | YES | 1920 | 55% | 50% | 60% | 15% | 480 | 480 | 1392.93 | 348.2325 | [7 empty] | 1392.93 | 348.2325
41 |  |  | Thomas BB | Plt04 | 65 | HEATER |  |  |  | HVAC | HEAT | AHD54 | Air Makeup (Heat-non-recirculating Gas Fired) MUA5 | 1 | 11000000 | 80% |  |  | V | YES | 8760 | 45% | 20% | 25% | 0% | 876 | 876 | 1355.0625 | 0 | [7 empty] | 1355.0625 | 0
42 |  |  | Thomas BB | Plt04 | 65 | HEATER |  |  |  | HVAC | HEAT | AHD55 | Air Makeup (Heat-non-recirculating Gas Fired) MUA4 | 1 | 11000000 | 80% |  |  | V | YES | 8760 | 45% | 20% | 25% | 0% | 876 | 876 | 1355.0625 | 0 | [7 empty] | 1355.0625 | 0
43 |  |  | Thomas BB | Plt04 | 65 | HEATER |  |  |  | HVAC | HEAT | AHD56 | Air Makeup (Heat-non-recirculating Gas Fired) MUA3 | 1 | 11000000 | 80% |  |  | V | YES | 8760 | 45% | 20% | 25% | 0% | 876 | 876 | 1355.0625 | 0 | [7 empty] | 1355.0625 | 0
44 |  |  | Thomas BB | Plt01 | 65 | HEATER |  |  |  | HVAC | HEAT | AHD57 | Air Makeup (Heat-non-recirculating Gas Fired) MUA6 | 1 | 11000000 | 80% |  |  | V | YES | 8760 | 45% | 20% | 25% | 0% | 876 | 876 | 1355.0625 | 0 | [7 empty] | 1355.0625 | 0
45 |  |  | Thomas BB | Plt01 | 65 | HEATER |  |  |  | HVAC | HEAT | AHD58 | Air Makeup (Heat-non-recirculating Gas Fired) MUA1 | 1 | 11000000 | 80% |  |  | V | YES | 8760 | 45% | 20% | 25% | 0% | 876 | 876 | 1355.0625 | 0 | [7 empty] | 1355.0625 | 0
46 |  |  | Thomas BB | Plt01 | 65 | HEATER |  |  |  | HVAC | HEAT | AHD59 | Air Makeup (Heat-non-recirculating Gas Fired) MUA2 | 1 | 11000000 | 80% |  |  | V | YES | 8760 | 45% | 20% | 25% | 0% | 876 | 876 | 1355.0625 | 0 | [7 empty] | 1355.0625 | 0
47 |  |  | Thomas BB | Plt01 | 25 | BOILER |  | Boiler Room | Boiler | BOILER | COMB | BLR000CONT01 | Boiler, Continental Automatic, Oil / Gas | 1 | 13800000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 25% | 0% | 1064 | 1064 | 2523.675 | 0 | [7 empty] | 2523.675 | 0
48 |  |  | Thomas BB | Plt02B | 30 | BOILER |  | TBB-PLT2B | Boiler | BOILER | COMB | BLR000-FF-03 | Boiler, Power Master Steam (ORR &Sembowers) | 1 | 8368750 | 80% |  |  | V | YES | 8760 | 55% | 60% | 30% | 0% | 2628 | 2628 | 4536.0717 | 0 | [7 empty] | 4536.0717 | 0
49 |  |  | Thomas BB | Plt01 | 15 | BOILER |  |  | Boiler | BOILER | COMB | BLR015SLR01 | Boiler, 15hp (Primeline) | 1 |  | 80% |  |  | V | YES | 3840 | 55% | 24.29% | 100% | 100% | 466.411 | 466.411 | 0 | 0 | [7 empty] | 0 | 0
50 |  |  | Thomas BB | Plt01 | 25 | BOILER |  | Boiler Room | Boiler | BOILER | COMB | BLR600CLVB01 | Boiler, Cleaver Brooks, 600HP | 1 | 25100000 | 80% |  |  | V | YES | 8760 | 55% | 60% | 30% | 0% | 2628 | 2628 | 13604.8275 | 0 | [7 empty] | 13604.8275 | 0
51 |  |  | Thomas BB | Plt01 | 15 | PAINT |  |  |  | OVEN | COMB | OV14 | Oven, Dry-Off (Primeline) | 1 | 10000000 | 80% |  |  | L | NO | 3840 | 55% | 100% | 60% | 40% | 1920 | 1920 | 7920 | 5280 | [7 empty] | 7920 | 5280
52 |  |  | Thomas BB | Plt01 | 14 | PAINT |  |  |  | OVEN | COMB | OV15 | Oven, Convection Bake (Yellow) | 1 | 7500000 | 80% |  |  | L | NO | 1920 | 55% | 100% | 60% | 15% | 960 | 960 | 2970 | 742.5 | [7 empty] | 2970 | 742.5
53 |  |  | Thomas BB | Plt01 | 14 | PAINT |  |  |  | OVEN | COMB | OV16 | Oven, Bake (White Roof) | 1 | 7500000 | 80% |  |  | L | NO | 1920 | 55% | 100% | 60% | 15% | 960 | 960 | 2970 | 742.5 | [7 empty] | 2970 | 742.5
54 |  |  | Thomas BB | Plt01 | 92 | PAINT |  |  |  | OVEN | COMB | OV17 | Oven, Convection Bake (Minotour Line) | 1 | 7500000 | 80% |  |  | L | NO | 1920 | 55% | 100% | 60% | 15% | 960 | 960 | 2970 | 742.5 | [7 empty] | 2970 | 742.5
55 |  |  | Thomas BB | Plt01 | 92 | PAINT |  |  |  | OVEN | COMB | OV18 | Oven, Bake (Minotour Line) | 1 | 7500000 | 80% |  |  | L | NO | 1920 | 55% | 100% | 60% | 15% | 960 | 960 | 2970 | 742.5 | [7 empty] | 2970 | 742.5
56 |  |  | Thomas BB | Plt01 | 15 | PAINT |  |  |  | OVEN | COMB | OV19 | Oven, Cure (Primeline) | 1 | 7500000 | 80% |  |  | L | NO | 3840 | 55% | 100% | 60% | 60% | 1920 | 1920 | 5940 | 5940 | [7 empty] | 5940 | 5940
57 |  |  | Thomas BB | Plt01 | 65 | HVAC |  |  | Combustion Side | HEAT | RADI |  | Co-Ray-Vac Radiant Heater | 25 | 100000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 100% | 0% | 1064 | 1064 | 1828.75 | 0 | [7 empty] | 1828.75 | 0
58 |  |  | Thomas BB | Plt04 | 65 | HVAC |  |  | Combustion Side | HEAT | RADI |  | Co-Ray-Vac Radiant Heater | 50 | 125000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 50% | 0% | 1064 | 1064 | 2285.9375 | 0 | [7 empty] | 2285.9375 | 0
59 |  |  | Thomas BB | Plt05 | 65 | HVAC |  |  | Combustion Side | HEAT | COMB |  | Unit Space Heater | 7 | 200000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 25% | 0% | 1064 | 1064 | 256.025 | 0 | [7 empty] | 256.025 | 0
60 |  |  | Thomas BB | Plt06 | 65 | HVAC |  |  | Combustion Side | HEAT | COMB |  | Unit Space Heater | 6 | 200000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 50% | 0% | 1064 | 1064 | 438.9 | 0 | [7 empty] | 438.9 | 0
61 |  |  | Thomas BB | Plt07 | 65 | HVAC |  |  | Combustion Side | HEAT | COMB |  | Unit Space Heater | 5 | 200000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 50% | 0% | 1064 | 1064 | 365.75 | 0 | [7 empty] | 365.75 | 0
|  |  | Thomas BB | Plt02A | B1 | [6 empty] | EQMCD02 | Generator, Natural Gas Backup (34kW) | 1 |  |  |  |  | I | NO | 8750
62 |  |  | Thomas BB | Plt02A | 65 | HVAC |  |  | Combustion Side | HEAT | RADI |  | Co-Ray-Vac Radiant Heater | 50 | 125000 | 80% |  |  | V | YES | 8760 | 55% | 24.29% | 80% | 10% | 1064 | 1064 | 3657.5 | 457.1875 | [7 empty] | 3657.5 | 457.1875
63 |  |  | Thomas BB | Plt02B | 65 | HVAC |  |  | Combustion Side | HEAT | RADI |  | Co-Ray-Vac Radiant Heater | 50 | 125000 | 48% |  |  | V | YES | 8760 | 80% | 24.29% | 80% | 15% | 1064 | 1064 | 8866.6667 | 1662.5 | [7 empty] | 8866.6667 | 1662.5
64 |  |  | Thomas BB | Plt02C | 65 | HVAC |  |  | Combustion Side | HEAT | RADI |  | Co-Ray-Vac Radiant Heater | 25 | 125000 | 48% |  |  | V | YES | 8760 | 80% | 24.29% | 80% | 15% | 1064 | 1064 | 4433.3333 | 831.25 | [7 empty] | 4433.3333 | 831.25
65 |  |  | Thomas BB | Plt02C | 65 | HVAC |  |  |  | HEAT | COMB |  | Heated Air Handler - Warm up bus under body | 1 | 3500000 | 80% |  |  | V | YES | 1920 | 100% | 24.29% | 100% | 100% | 233.2055 | 233.2055 | 1020.274 | 1020.274 | [7 empty] | 1020.274 | 1020.274
66 |  |  | Thomas BB | Plt01 | 15 | OVEN |  |  |  | OVEN | COMB |  | Dry-Off Oven - Powder Paint Prime Line | 1 |  | 80% |  |  | L | NO | 8760 | 100% | 24.29% | 100% | 100% | 1064 | 1064 | 0 | 0 | [7 empty] | 0 | 0
67 |  |  | Thomas BB | Plt01 | 15 | OVEN |  |  |  | OVEN | COMB |  | Curing Oven - Powder Paint Prime Line | 1 |  | 80% |  |  | L | NO | 8760 | 100% | 24.29% | 100% | 100% | 1064 | 1064 | 0 | 0 | [7 empty] | 0 | 0
68 |  |  | Thomas BB | Plt04 | 65 | HVAC |  |  |  | HEAT | COMB |  | Space Heaters | 7 | 250000 | 80% |  |  | V | YES | 8760 | 55% | 100% | 35% | 0% | 4380 | 4380 | 1844.3906 | 0
69 |  |  | Thomas BB
84 |  |  | Thomas BB
| INSERT LINES ONLY - DO NOT DRAG DOWN | [17 empty] | INFO Only | INFO Only |  | Changes MMBTU | Changes Hours | Changes MMBTU | Changes MMBTU |  | N.G. TOTALS | 138220.242 | 28472.1605 | 166692.4024 | [6 empty] | 136375.8513 | 28472.1605
[28 empty] | Winter | Summer | [8 empty] | 164848.0118
[28 empty] | MMBTU | MMBTU
[27 empty] | Vehicle | LP | LP
[28 empty] | 0 | 0 | 0 | 166692.4024
[8 empty] | SEASONAL Effected Load | [19 empty] | 0% | 0%
|  |  | Site Pull Down |  | OPS CODE Pull DOWN |  |  | Sub-Metered Load | [18 empty] | Vehicle | DIESEL | DIESEL
[8 empty] | YES | [19 empty] | 0 | 0 | 0
|  |  | Thomas Built Buses |  | B |  |  | NO | [19 empty] | 0% | 0%
|  |  | FCCC |  | I
|  |  | Gastonia |  | L | [21 empty] | The tables below are created manually by sorting the above lines.
|  |  | HQ-Fort Mill |  | V | [21 empty] | These do not update automatically.
|  |  | HQ-Portland | [23 empty] | The data from the tables below are used to create Energy USE pie charts.
|  |  | Mt Holly | [22 empty] | DONE | DEPT | SYSTEM
|  |  | Portland | [22 empty] | 2020-07-24 | SORT 1 | SORT 2 | MMBTU | # of Line Items
|  |  | Santiago | [22 empty] | MUA Heating | ALL | AMU/AHU | 53372 | 20
|  |  | Saltillo | [22 empty] | Space Heating | ALL | BOILER | 20665 | 4
|  |  | Thomas BB | [22 empty] | MUA Heating | ALL | HEATER | 8130 | 6
[26 empty] | Space Heating | ALL | HVAC | 33650 | 12
[26 empty] | Ovens | ALL | PAINT | 50875 | 11
ALL
[28 empty] | TOTALS | 166692 | 53 | 53 | lines
166692.4024
0.40245
CHECKS
[27 empty] | KEY 1 | KEY 2
[27 empty] | SORT 1 | SORT 2 | MMBTU | # of Line Items
[27 empty] | BOILER | COMB | 20665 | 4
[27 empty] | HEAT | COMB & RADI | 28969 | 10
[27 empty] | HVAC | HEATING | 66184 | 28
[27 empty] | PAINT | COMB | 50875 | 11
[28 empty] | TOTALS | 166693 | 53
166692.4024
-0.59755
CHECKS
Note on V9: Author: Default of 365 days times 24 hours per day
Note on AJ9: Author: Convert from meter units to MMBTU, as needed
Note on AK9: Author: Convert from meter units to MMBTU, as needed
Note on D10: Author: Pull down menu.
Note on E10: Author: Name or Number
Note on J10: Author: This is the item actually consuming the electricity
Note on Q10: Author: Estimated combustion efficiency. Or actual data, if known.
Note on W10: Author: Typically, if you have a diversity factor < 100% you will NOT also derate load factor. Only one or the other of DF or LF should be derated.
Note on X10: Author: This defaults to the value in cell S7. Enter manually if different.
Note on Y10: Author: Only one or the other of DF or LF should be derated.
Note on Z10: Author: Only one or the other of DF or LF should be derated.

## 3E_Diversity Factor
3E
Diversity Factor Examples
Reference Info
The two examples below demonstrate the diversity factor and how to estimate this.
|  | Electric | [5 empty] | Natural Gas
| 1,000 kwh Electric Oven | [5 empty] | 1,000,000 BTU/HR Natural Gas Oven
| Operational Temperature: 450 ºF | [5 empty] | Operational Temperature: 450 ºF
|  |  | Oven |  |  |  |  | BTU/HR | Oven
| Hour | kW | Temp |  |  |  | Hour | Rate | Temp
| 0 | 0 | 80 |  | Total kWh |  | 0 | 0 | 80 | Total BTU
| 1 | 1000 | 400 |  | 5500 |  | 1 | 1000000 | 160 | 6000000
| 2 | 700 | 450 |  | 750 |  | 2 | 1000000 | 240 | 4500000
| 3 | 500 | 448 |  | 6250 |  | 3 | 1000000 | 320 | 10500000
| 4 | 450 | 452 |  |  |  | 4 | 1000000 | 420
| 5 | 500 | 448 |  | 520.8333 | Average kW | 5 | 750000 | 450 | 656250 | Average BTU/hour
| 6 | 450 | 452 |  | 52.08% |  | 6 | 450000 | 445 | 65.62%
| 7 | 500 | 448 |  | D.F. |  | 7 | 500000 | 455 | D.F.
| 8 | 450 | 452 |  |  |  | 8 | 450000 | 445
| 9 | 500 | 448 |  |  |  | 9 | 500000 | 455
| 10 | 450 | 452 |  |  |  | 10 | 450000 | 445
| 11 | 500 | 448 |  |  |  | 11 | 500000 | 455
| 12 | 0 | 80 |  |  |  | 12 | 450000 | 445
[7 empty] | 13 | 500000 | 455
[7 empty] | 14 | 400000 | 445
[7 empty] | 15 | 0 | 300
[7 empty] | 16 | 0 | 150

## 4_Utility Data
4 |  | DTNA Site:
Energy Mapping Process for Daimler Truck North America
Utility Data and Relevant Variables
Cut and Paste, or link this tab to your EnPI model "Input Raw Data" Tab
All plants have EnPI models with this information already collected.
See example below from the Thomas Built Buses Plant EnPI Model, first tab
Thomas Built Buses Site Input Raw Data table from the EnPI Model
|  |  | Energy Input Data |  |  |  | Possible Relevant Variables
|  |  |  | PRIMARY (*3) |  |  | PRODUCTION | PRODUCTION | PRODUCTION |  |  |  | TOTAL ENERGY
|  | Actual Date * | Electricity (kWh site) | Electricity (MMBTU) | Natural Gas (kWh) | Natural Gas (MMBTU) | Trucks (count) | Manhours | Paint (Gallons) | Heating Degree Days (HDD) | Cooling Degree Days (CDD) | Period | MMBTU (Site)
|  | 2013-01-01 | 2431802 | 24892.9612 | 6792483.39 | 23176.9179 | 870 | 216968.4834 | 3728.25 | 625 | 1 | 2013-01-01 | 31474.5716
|  | 2013-02-01 | 2495010.5 | 25539.9904 | 5989237.134 | 20436.1276 | 816 | 167065.1914 | 3204.625 | 641 | 0 | 2013-02-01 | 28949.4577
|  | 2013-03-01 | 2380543 | 24368.2523 | 5751088.452 | 19623.5305 | 928 | 206791.9318 | 3523.75 | 590 | 0 | 2013-03-01 | 27746.2812
|  | 2013-04-01 | 2195982.5 | 22479.0124 | 3020555.262 | 10306.5635 | 988 | 211858.4283 | 3966.155 | 173 | 47 | 2013-04-01 | 17799.5676
|  | 2013-05-01 | 3336214 | 34150.9077 | 1819906.086 | 6209.778 | 1159 | 251806.6206 | 4411.375 | 80 | 108 | 2013-05-01 | 17593.4139
|  | 2013-06-01 | 3021647.5 | 30930.871 | 1460836.722 | 4984.5823 | 1246.5 | 262632.5385 | 4807.5 | 0 | 293 | 2013-06-01 | 15294.8727
|  | 2013-07-01 | 3099182 | 31724.5472 | 1624897.308 | 5544.3804 | 1216.5 | 262319.5542 | 4657.875 | 0 | 403 | 2013-07-01 | 16119.2294
|  | 2013-08-01 | 3014185 | 30854.4817 | 1173012.675 | 4002.4858 | 859.5 | 201674.0096 | 3216.1875 | 0 | 319 | 2013-08-01 | 14287.313
|  | 2013-09-01 | 2732105.5 | 27966.9958 | 1284965.415 | 4384.4845 | 984.5 | 216217.9108 | 3637.84 | 10 | 183 | 2013-09-01 | 13706.8164
|  | 2013-10-01 | 2694038.5 | 27577.3257 | 2482683.891 | 8471.27 | 1068 | 244953.6495 | 4198.625 | 130 | 53 | 2013-10-01 | 17663.7119
|  | 2013-11-01 | 2571190.5 | 26319.8013 | 5220045.612 | 17811.5369 | 881.5 | 198472.4091 | 3297.0675 | 517 | 2 | 2013-11-01 | 26584.804
|  | 2013-12-01 | 2555012.5 | 26154.1964 | 5840386.881 | 19928.2294 | 818.5 | 173684.2098 | 2858.5625 | 599 | 5 | 2013-12-01 | 28646.2948
|  | 2014-01-01 | 2425332 | 24826.7315 | 8347190.433 | 28481.7991 | 843 | 226796.5166 | 3564 | 924 | 0 | 2014-01-01 | 36757.3762
|  | 2014-02-01 | 2617217.5 | 26790.9533 | 6444638.607 | 21990.0221 | 899 | 175741.8086 | 3520.625 | 566 | 0 | 2014-02-01 | 30920.3398
|  | 2014-03-01 | 2415086 | 24721.8491 | 6705734.67 | 22880.9189 | 988 | 225628.0682 | 3787 | 529 | 1 | 2014-03-01 | 31121.5353
|  | 2014-04-01 | 2343559.5 | 23989.6734 | 2730122.892 | 9315.567 | 1099 | 243007.5717 | 4321.5 | 168 | 26 | 2014-04-01 | 17312.1248
|  | 2014-05-01 | 3329543 | 34082.6205 | 1566488.457 | 5345.0811 | 1171 | 261335.3794 | 4542.25 | 31 | 191 | 2014-05-01 | 16705.9546
|  | 2014-06-01 | 3026727.5 | 30982.8721 | 1269843.003 | 4332.8846 | 1239.5 | 265209.4615 | 4627.25 | 0 | 331 | 2014-06-01 | 14660.5087
|  | 2014-07-01 | 3193829 | 32693.3942 | 1250060.778 | 4265.3849 | 1258.5 | 268280.4458 | 4658 | 0 | 365 | 2014-07-01 | 15163.183
|  | 2014-08-01 | 3022575 | 30940.3653 | 1068269.457 | 3645.0871 | 853.5 | 204746.9904 | 3108.25 | 0 | 328 | 2014-08-01 | 13958.5422
|  | 2014-09-01 | 2852549.5 | 29199.9119 | 1442754.303 | 4922.8826 | 1037.5 | 236572.0892 | 3820.125 | 7 | 212 | 2014-09-01 | 14656.1865
|  | 2014-10-01 | 2833648.5 | 29006.4332 | 2767372.089 | 9442.6665 | 1093 | 254991.3505 | 4161.25 | 112 | 51 | 2014-10-01 | 19111.4776
|  | 2014-11-01 | 2678732.5 | 27420.647 | 5519475.231 | 18833.2333 | 894.5 | 208065.5909 | 3314.875 | 532 | 0 | 2014-11-01 | 27973.4489
|  | 2014-12-01 | 2630365.5 | 26925.5418 | 5463410.94 | 18641.9339 | 801.5 | 185303.7902 | 2952.125 | 616 | 0 | 2014-12-01 | 27617.1145
|  | 2015-01-01 | 2530265 | 25900.8704 | 7757211.216 | 26468.7062 | 667 | 215553 | 2581.3075 | 772 | 0 | 2015-01-01 | 35102.3297
|  | 2015-02-01 | 2737850 | 28025.7989 | 8183686.68 | 27923.901 | 711 | 207536 | 2927.855 | 813 | 0 | 2015-02-01 | 37265.834
|  | 2015-03-01 | 2778009 | 28436.8836 | 5309988.795 | 18118.4358 | 1056 | 273600 | 4440.4475 | 376 | 2 | 2015-03-01 | 27597.397
|  | 2015-04-01 | 2903015 | 29716.4982 | 2724261.492 | 9295.5671 | 1033 | 268565 | 4094.1875 | 139 | 45 | 2015-04-01 | 19201.0665
|  | 2015-05-01 | 3047409 | 31194.5767 | 1563264.687 | 5334.0811 | 1068 | 278780 | 4220.2325 | 15 | 186 | 2015-05-01 | 15732.2733
|  | 2015-06-01 | 3194119 | 32696.3628 | 1293464.445 | 4413.4844 | 1165 | 294343 | 4655.6125 | 0 | 385 | 2015-06-01 | 15312.272
|  | 2015-07-01 | 3373419 | 34531.754 | 1348561.605 | 4601.4837 | 1122 | 310535 | 4756.9075 | 0 | 443 | 2015-07-01 | 16112.0683
|  | 2015-08-01 | 3457743 | 35394.9303 | 1392258.342 | 4750.5832 | 1163 | 310353 | 4720.85 | 0 | 377 | 2015-08-01 | 16548.8933
|  | 2015-09-01 | 3242689 | 33193.546 | 1661443.137 | 5669.0799 | 1223 | 293690 | 4789.36 | 4 | 233 | 2015-09-01 | 16733.5952
|  | 2015-10-01 | 3044702 | 31166.8667 | 3102790.704 | 10587.1625 | 1298 | 305152 | 5058.7075 | 145 | 22 | 2015-10-01 | 20976.1181
|  | 2015-11-01 | 2910326 | 29791.3367 | 3995394.003 | 13632.8517 | 1064 | 305152 | 4074.5275 | 302 | 8 | 2015-11-01 | 23563.2973
|  | 2015-12-01 | 2889355 | 29576.6686 | 4338842.736 | 14804.7475 | 1007 | 234278 | 3937.4525 | 332 | 13 | 2015-12-01 | 24663.6371
|  | 2016-01-01 | 2671904 | 27350.7476 | 7519033.227 | 25656.0091 | 1072 | 271432 | 4138.5833 | 811 | 0 | 2016-01-01 | 34772.9249
|  | 2016-02-01 | 2984229 | 30547.8393 | 6449415.648 | 22006.322 | 1310 | 299860 | 4915.8333 | 630 | 0 | 2016-02-01 | 32188.9351
|  | 2016-03-01 | 3103631 | 31770.0891 | 3710823.033 | 12661.8551 | 1430 | 323940 | 5237.8333 | 233 | 24 | 2016-03-01 | 23251.8848
|  | 2016-04-01 | 3144734 | 32190.8369 | 2477877.543 | 8454.87 | 1429 | 328507 | 5143.8333 | 169 | 60 | 2016-04-01 | 19185.149
|  | 2016-05-01 | 3107949 | 31814.29 | 1804490.604 | 6157.1782 | 1369 | 339261 | 5013.5833 | 54 | 104 | 2016-05-01 | 16761.9415
|  | 2016-06-01 | 3489940 | 35724.5126 | 1442519.847 | 4922.0826 | 1456 | 353870 | 5502.5833 | 0 | 349 | 2016-06-01 | 16830.2534
|  | 2016-07-01 | 3379095 | 34589.8559 | 1130224.455 | 3856.4863 | 1132 | 302395 | 4321.5833 | 0 | 510 | 2016-07-01 | 15386.4383
|  | 2016-08-01 | 3829945 | 39204.9486 | 1519099.038 | 5183.3816 | 1607 | 392557 | 5936.5833 | 0 | 480 | 2016-08-01 | 18251.6978
|  | 2016-09-01 | 3588851 | 36737.0077 | 1355155.68 | 4623.9836 | 1346 | 339651 | 5132.5833 | 0 | 336 | 2016-09-01 | 16869.6528
|  | 2016-10-01 | 3268723 | 33460.0411 | 2260155.84 | 7711.9727 | 1366 | 317748 | 5105.5833 | 97 | 57 | 2016-10-01 | 18865.3197
|  | 2016-11-01 | 3181064 | 32562.7262 | 4284507.558 | 14619.3482 | 1257 | 294365 | 4774.5833 | 277 | 8 | 2016-11-01 | 25473.5903
|  | 2016-12-01 | 3022240 | 30936.9361 | 5956032.303 | 20322.828 | 984 | 237928 | 3584.5833 | 624 | 0 | 2016-12-01 | 30635.14
|  | 2017-01-01 | 2903985 | 29726.4276 | 5876287.956 | 20050.7289 | 1424 | 333465 | 5313.9 | 572 | 0 | 2017-01-01 | 29959.5381
|  | 2017-02-01 | 3092274 | 31653.834 | 5225848.398 | 17831.3368 | 1382 | 315954 | 5146.7 | 342 | 5 | 2017-02-01 | 28382.6148
|  | 2017-03-01 | 3124131 | 31979.9358 | 5487823.671 | 18725.2336 | 1660 | 381059 | 6184.7 | 383 | 9 | 2017-03-01 | 29385.2122
|  | 2017-04-01 | 3405159 | 34856.6581 | 2328089.466 | 7943.7718 | 1488 | 343032 | 5603.7 | 123 | 62 | 2017-04-01 | 19562.6579
|  | 2017-05-01 | 3419514 | 35003.602 | 1768970.52 | 6035.9786 | 1633 | 413284 | 6241 | 43 | 159 | 2017-05-01 | 17703.8459
|  | 2017-06-01 | 3666215 | 37528.9385 | 1386660.705 | 4731.4832 | 1583 | 378160 | 6168.3 | 0 | 280 | 2017-06-01 | 17241.1294
|  | 2017-07-01 | 3341636 | 34206.4096 | 1080578.397 | 3687.0869 | 1174 | 277305 | 4613.8 | 0 | 451 | 2017-07-01 | 15089.2235
|  | 2017-08-01 | 3823243 | 39136.344 | 1441992.321 | 4920.2826 | 1635 | 374941 | 6417.3 | 0 | 367 | 2017-08-01 | 17965.7306
|  | 2017-09-01 | 3247853 | 33246.4069 | 1098338.439 | 3747.6867 | 1059 | 247653 | 4038.4 | 11 | 205 | 2017-09-01 | 14829.8223
|  | 2017-10-01 | 3218244 | 32943.3166 | 3127672.347 | 10672.0622 | 1409 | 338166 | 5302.9 | 119 | 88 | 2017-10-01 | 21653.1677 | SITE | SITE
|  | 2017-11-01 | 3098394 | 31716.4809 | 4676430.069 | 15956.6434 | 1192 | 284648 | 4485.3 | 395 | 2 | 2017-11-01 | 26528.8037 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2017-12-01 | 3110229 | 31837.629 | 6548473.308 | 22344.3208 | 996 | 245872 | 3835.6 | 678 | 0 | 2017-12-01 | 32956.8638 | 39450877 | 136646.6157
|  | 2018-01-01 | 2933926 | 30032.9164 | 8136267.954 | 27762.1016 | 1135 | 284124 | 4703.11 | 859 | 0 | 2018-01-01 | 37773.0737
|  | 2018-02-01 | 3114294 | 31879.2401 | 4769421.18 | 16273.9423 | 1273 | 298154 | 4656.4 | 380 | 14 | 2018-02-01 | 26900.3557
|  | 2018-03-01 | 2979818 | 30502.6865 | 5636117.091 | 19231.2318 | 1245 | 298799 | 4800.2 | 547 | 6 | 2018-03-01 | 29398.794
|  | 2018-04-01 | 3203583 | 32793.2403 | 3251904.72 | 11095.9607 | 1385 | 321311 | 5279.2 | 216 | 22 | 2018-04-01 | 22027.0408
|  | 2018-05-01 | 3448943 | 35304.8498 | 1555937.937 | 5309.0812 | 1455 | 333263 | 5492.5 | 2 | 264 | 2018-05-01 | 17077.3645
|  | 2018-06-01 | 3675393 | 37622.8885 | 1356503.802 | 4628.5836 | 1383 | 337613 | 5563.4 | 0 | 393 | 2018-06-01 | 17169.5464
|  | 2018-07-01 | 3401017 | 34814.2588 | 1195256.688 | 4078.3855 | 1149 | 301700 | 4722.4 | 0 | 423 | 2018-07-01 | 15683.1385
|  | 2018-08-01 | 3916687 | 40092.8766 | 1420129.299 | 4845.6828 | 1455 | 359932 | 5585.6 | 0 | 378 | 2018-08-01 | 18209.975
|  | 2018-09-01 | 3222418 | 32986.0434 | 956258.103 | 3262.8884 | 877 | 245572 | 3499.66 | 0 | 345 | 2018-09-01 | 14258.2362
|  | 2018-10-01 | 3215750 | 32917.7869 | 3359344.182 | 11462.5594 | 1191 | 312358 | 4827.13 | 176 | 124 | 2018-10-01 | 22435.155 | SITE | SITE
|  | 2018-11-01 | 2884541 | 29527.3905 | 6558115.311 | 22377.2207 | 1111 | 267062 | 4291.95 | 522 | 2 | 2018-11-01 | 32219.6842 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2018-12-01 | 2757501 | 28226.9549 | 6778416.03 | 23128.918 | 846 | 222123 | 3131.9766 | 644 | 0 | 2018-12-01 | 32537.903 | 38753871 | 153456.5561
|  | 2019-01-01 | 2619064 | 26809.8548 | 9334777.719 | 31851.5871 | 1382 | 308553 | 4845.8759 | 711 | 0 | 2019-01-01 | 40788.2054
|  | 2019-02-01 | 2792964 | 28589.9693 | 7273147.497 | 24817.012 | 1199 | 271529 | 4163.0621 | 459 | 4 | 2019-02-01 | 34347.0018
|  | 2019-03-01 | 2631379 | 26935.9164 | 6231225.033 | 21261.8246 | 1260 | 271028 | 4271.1863 | 469 | 0 | 2019-03-01 | 30240.4635
|  | 2019-04-01 | 2831058 | 28979.9157 | 2870649.957 | 9795.0653 | 1334 | 311845 | 4664.0785 | 110 | 50 | 2019-04-01 | 19455.0372
|  | 2019-05-01 | 2972870 | 30431.5638 | 1833094.236 | 6254.7778 | 1373 | 307475 | 4913.6591 | 9 | 270 | 2019-05-01 | 16398.6324
|  | 2019-06-01 | 2987452 | 30580.8313 | 1326962.346 | 4527.784 | 1249 | 249265 | 4631.4723 | 0 | 309 | 2019-06-01 | 14721.3944
|  | 2019-07-01 | 2834569 | 29015.8558 | 1192853.514 | 4070.1856 | 1094 | 223629 | 4043.2862 | 0 | 0 | 2019-07-01 | 13742.1375
|  | 2019-08-01 | 3207330 | 32831.5962 | 1309817.751 | 4469.2842 | 1230 | 243729 | 4173.0382 | 0 | 412 | 2019-08-01 | 15413.1496
|  | 2019-09-01 | 2558103 | 26185.8321 | 1209968.802 | 4128.5854 | 821 | 202753 | 3095.6897 | 0 | 373 | 2019-09-01 | 12857.1961
|  | 2019-10-01 | 2521210 | 25808.1796 | 3518070.894 | 12004.1575 | 1242 | 252476 | 4284.7454 | 0 | 0 | 2019-10-01 | 20606.884 | SITE | SITE
|  | 2019-11-01 | 2389782 | 24462.8266 | 5890472.544 | 20099.1288 | 1055 | 240524 | 3763.4059 | 0 | 0 | 2019-11-01 | 28253.4043 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2019-12-01 | 2170379 | 22216.924 | 5658507.639 | 19307.6316 | 872 | 208249 | 3199.8931 | 605 | 0 | 2019-12-01 | 26713.2729 | 32516160 | 162587.0238
|  | 2020-01-01 | 2134150 | 21846.0685 | 7155978.111 | 24417.2135 | 1296 | 269577 | 4603.5605 | 583 | 0 | 2020-01-01 | 31699.2363
|  | 2020-02-01 | 0 | 0 | 0 | 0 | 1208 | 287359 | 5168.441 |  |  | 2020-02-01 | 0
|  | 2020-03-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2020-03-01 | 0
|  | 2020-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2020-04-01 | 0
|  | 2020-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2020-05-01 | 0
|  | 2020-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2020-06-01 | 0
|  | 2020-07-01 | [9 empty] | 2020-07-01 | 0
|  | 2020-08-01 | [9 empty] | 2020-08-01 | 0
|  | 2020-09-01 | [9 empty] | 2020-09-01 | 0
|  | 2020-10-01 | [9 empty] | 2020-10-01 | 0 | SITE | SITE
|  | 2020-11-01 | [9 empty] | 2020-11-01 | 0 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2020-12-01 | [9 empty] | 2020-12-01 | 0 | 2134150 | 24417.2135
|  | 2021-01-01 | [9 empty] | 2021-01-01
|  | 2021-02-01 | [9 empty] | 2021-02-01
|  | 2021-03-01 | [9 empty] | 2021-03-01
|  | 2021-04-01 | [9 empty] | 2021-04-01
|  | TOTALS | 253632343 | 2596288.7103 | 309442326.243 | 1055861.158 | 100104 | 23632716 | 380676.7807 | 21601 | 11578

## 5_Estimated vs Actual
5 | DTNA Site:
Energy Mapping Process for Daimler Truck North America
|  | Estimated versus Actual |  |  | GRAND TOTALS
This is used to compare you measured and estimated energy consumption at end uses to the actual total energy that you were billed for
For example if your total site electrical bills for the year add up to 65,000,000 kwh, your goal will be for you electrical energy consumption estimate to be close to this same number
The Thomas Built Buses and Mount Holly site energy mapping spreadsheets have a tab for this.
SITE LEVEL
|  |  | ELECTRICITY |  |  |  | CONVERT Electrical to MMBTU
|  |  |  | Total Estimated ANNUAL kWh from Tab 3C: | 0 | kWh | 0 | MMBTU
|  |  |  | Total actual ANNUAL kWh from Duke Energy invoices: | 32516160 | kWh | 110949.6902 | MMBTU
2019
|  |  |  | DELTA: | -32516160 | -100%
NATURAL GAS
|  |  |  | Total Estimated ANNUAL MMBTU from Tab 3D: | 166692.4024 | MMBTU
|  |  |  | Total actual ANNUAL MMBTU from all natural gas invoices: | 162587.0238 | MMBTU
|  |  |  | 2019 |  |  |  |  | 1873
|  |  |  | DELTA: | 4105.3787 | 2.525%
OTHER COMBUSTION FUELS (LP, Diesel)
|  |  |  | Total Estimated ANNUAL MMBTU from Tab 3D: | 0 | MMBTU
|  |  |  | Total actual ANNUAL MMBTU from invoices: | 0 | MMBTU
2019
|  |  |  | DELTA: | 0 | #DIV/0!
|  |  |  | GRAND TOTAL Estimate: | 166692.4024 | MMBTU
|  |  |  | GRAND TOTAL Actual: | 273536.714 | MMBTU
2019
|  |  |  | Grand Total DELTA: | -106844.3115 | -39.06%

## 6_Two Key Pies
6 | DTNA Site:
Energy Mapping Process for Daimler Truck North America
Create the TWO key Pie Charts
Where does all the energy go? - Continued
|  |  |  | IN | [6 empty] | By INVOICES
[9 empty] | TOTAL energy IN | Type | MMBTU | %
[10 empty] | Liquid Propane | 0 | 0%
[10 empty] | Diesel Fuel | 0 | 0%
[9 empty] | SITE | Electricity | 110949.6902 | 40.56% |  | 32516160 | kwh
[10 empty] | Natural Gas | 162587.0238 | 59.44%
[11 empty] | 273536.714 | 100%
|  |  |  | USED | [7 empty] | SORT
[9 empty] | TOTAL energy used from ALL TYPES | By system |  | High to Low
TOTAL
[6 empty] | Energy Type |  |  |  | DEPT | SYSTEM | ESTIMATED
[5 empty] | # | E | NG | LP | D | SORT 1 | SORT 2 | MMBTU | % | Energy Use
[5 empty] | 1 | X | X |  |  | FACILITY | HEATING | 95236.4 | 34.57% | MUA and Space Heating
[5 empty] | 2 | X | X |  |  | MANF | PAINT | 55762 | 20.24% | PAINTING OVENS
[5 empty] | 3 | X |  |  |  | FACILITY | FANS | 39176.5 | 14.22% | Exhaust and Ventilation Fans
[5 empty] | 4 | X |  |  |  | MANF | WELD | 21203.5 | 7.697% | WELDING
[5 empty] | 5 | X | X |  |  | FACILITY | BOILER | 20783.1 | 7.544% | BOILERS
[5 empty] | 6 | X |  |  |  | FACILITY | AC Units | 10414.7 | 3.78% | Air Conditioning Units
[5 empty] | 7 | X |  |  |  | FACILITY | C. AIR | 10037.6 | 3.644% | COMPRESSED AIR
[5 empty] | 8 | X |  |  |  | MANF | MACHINERY | 8795 | 3.192% | MANF Machinery
[5 empty] | 9 | X |  |  |  | FACILITY | CHILL | 8565.3 | 3.109% | Chillers and Pumps
[5 empty] | 10 | X |  |  |  | FACILITY | LIGHTING | 5518.4 | 2.003% | LIGHTING
11
12
13
14
15
16
17
18
19
20
[12 empty] | 275492.5 | 100%
108800.0976
CHECKs, if ZERO
[9 empty] | TOTAL energy used from ELECTRIC | By End Use
[10 empty] | KEY 1 | KEY 2 | ELEC EQUIV
[10 empty] | SORT 1 | SORT 2 | MMBTU | %
[10 empty] | MOTOR | All Types | 79452.9 | 73.03% | Motors
[10 empty] | WELDING | All Types | 21203.5 | 19.49% | Welding
[10 empty] | LIGHT | All Types | 5518.4 | 5.072% | Lighting
[10 empty] | ELEC | OTHER | 2626 | 2.414% | Other Electric
[12 empty] | 108800.8 | 100%
108800.8
CHECKS
[9 empty] | TOTAL energy used by MOTORS | By End Use
[10 empty] | KEY 1 | KEY 2 | ELEC EQUIV
[10 empty] | SORT 1 | SORT 2 | MMBTU | %
[10 empty] | MOTOR | HVAC | 36430.6 | 45.85% | HVAC
[10 empty] | MOTOR | FAN | 22725 | 28.6% | Fans
[10 empty] | MOTOR | C. AIR | 10037.6 | 12.63% | Compressed Air
[10 empty] | MOTOR | MAT HAND | 6160 | 7.753% | Material Handling
[10 empty] | MOTOR | PUMP | 3657.8 | 4.604% | Pumps
[10 empty] | MOTOR | BLOWER | 442.4 | 0.5568% | Blowers
[12 empty] | 79453.4 | 100%
0
CHECKS
REFERENCE INFO
For Electricity
[10 empty] | 1 | kWh | = | 3412 | BTU
[11 empty] | Energy |  |  | Energy
e.g.
[10 empty] | 1000000 | kWh | = | 3412 | MMBTU
[10 empty] | 5000000 | kWh | = | 17060 | MMBTU
Diesel
139000
BTU per gallon
LP
91330
BTU per gallon

## 7_SEUs
7 |  | DTNA Site: | [8 empty] | From ISO 50001 | 3.5.6 | significant energy use |  | SEU
|  | Energy Mapping Process for Daimler Truck North America | [9 empty] | energy use (3.5.4) accounting for substantial energy consumption (3.5.2) and/or offering considerable potential for energy performance improvement (3.4.6)
Note 1 to entry: Significance criteria are determined by the organization (3.1.1).
|  |  | Determination of SEUs | [8 empty] | Note 2 to entry: SEUs can be facilities, systems, processes, or equipment.
Use the consumption pie chart
|  |  |  | This tab creates a table from the consumption pie chart | [9 empty] | SEU SCORING CRITERIA
|  |  |  | Ranked by total combined energy from all types for specifc energy uses | [8 empty] | Consumption Rank
[15 empty] | Greater than 20% | 10
[10 empty] | Calculated score |  |  |  |  | Greater than 15%, but < 20% | 7
|  |  | SORT | [6 empty] | Site scored |  |  |  |  | Greater than10%, but < 15% | 5
|  |  | ESTIMATED | [11 empty] | Greater than 1%, but < 10% | 2
|  |  | Annual | [5 empty] | SEU SCORING | Improvement |  |  |  |  | Less than 1% | 0.5
|  |  | Consumption | Energy Types Consumed |  |  |  | Consumption | Consumption | Potential | TOTAL | OVERALL
| # | Energy Use | (MMBTU) | ELEC | N. Gas | LP | Diesel | Percentage | Rank | Rank* | SCORE | RANK |  | Improvement Potential Rank*
| 1 | MUA and Space Heating | 95236.4 | X | X | - | - | 34.57% | 10 | 70 | 700 | 1 |  |  | This rank will be entered by the site.
| 2 | PAINTING OVENS | 55762 | X | X | - | - | 20.24% | 10 | 70 | 700 | 1 |  |  | This is based on the perceived or actual level of potential to improve energy performance.
| 3 | Exhaust and Ventilation Fans | 39176.5 | X | - | - | - | 14.22% | 5 | 70 | 350 | 2 |  |  | An energy use with a lower consumption could have an excellent improvement potential.
| 4 | WELDING | 21203.5 | X | - | - | - | 7.697% | 2 | 30 | 60 |  |  |  | Rank the area from 1 to 10 based on the potential for energy performance improvement.
| 5 | BOILERS | 20783.1 | X | X | - | - | 7.544% | 2 | 70 | 140 | 4 |  |  |  | Estimated improvement of > 30% to baseline: | 100
| 6 | Air Conditioning Units | 10414.7 | X | - | - | - | 3.78% | 2 | 70 | 140 | 4 |  |  |  | Estimated improvement of 20 - 30% to baseline: | 70
| 7 | COMPRESSED AIR | 10037.6 | X | - | - | - | 3.644% | 2 | 100 | 200 | 3 |  |  |  | Estimated improvement of 10 - 20% to baseline: | 50
| 8 | MANF Machinery | 8795 | X | - | - | - | 3.192% | 2 | 100 | 200 | 3 |  |  |  | Estimated improvement of up to 10% to baseline: | 30
| 9 | Chillers and Pumps | 8565.3 | X | - | - | - | 3.109% | 2 | 50 | 100 |  |  |  |  | Very limited opportunity at this time: | 1
| 10 | LIGHTING | 5518.4 | X | - | - | - | 2.003% | 2 | 50 | 100
| 11 |  | 0 | - | - | - | - | 0%
| 12 |  | 0 | - | - | - | - | 0%
| 13 |  | 0 | - | - | - | - | 0%
| 14 |  | 0 | - | - | - | - | 0%
| 15 |  | 0 | - | - | - | - | 0%
| 16 |  | 0 | - | - | - | - | 0%
| 17 |  | 0 | - | - | - | - | 0%
| 18 |  | 0 | - | - | - | - | 0%
| 19 |  | 0 | - | - | - | - | 0%
| 20 |  | 0 | - | - | - | - | 0%
|  |  | 275492.5 |  |  |  |  | 100%
|  |  | CHECK |  |  |  |  | CHECK
SELECTED SEUs
1
2
3
|  |  | NOTE: | The above table is filled out through discussion and agreement of the Energy Team

## 7A_SEU Actions
7A |  | DTNA Site: |  |  | REFERENCE INFORMATION
Energy Mapping Process for Daimler Truck North America
Follow on actions REQUIRES for your selected SEUs.
|  |  | Significant Energy Uses (SEUs) |  |  | UPDATED for ISO 50001: 2018
The ISO 50001: 2018 standard requires you to identify SEUs for your plant operations.
Once you have designated these SEUs, there are additional requirements for work to be done for each of these SEUs.
|  |  | DEFINITION | 3.5.6 significant energy use (SEU)
|  |  | from the ISO 50001: | energy use (3.5.4) accounting for substantial energy consumption (3.5.2) and/or offering considerable potential for energy performance improvement (3.4.6)
|  |  | 2018 Standard | Note 1 to entry: Significance criteria are determined by the organization (3.1.1).
Note 2 to entry: SEUs can be facilities, systems, processes, or equipment.
| Item | PDCA | 50001 Ready | ISO 50001
| # | Step | Step(s) | Section | Direct Text from the ISO 50001: 2018 Standard | Comments
| 1 | PLAN | 12 | 6.2 Objectives, energy targets and planning to achieve them | 6.2.2 The objectives and energy targets shall: a) …. d) consider SEUs (see 6.3) | You must consider and take in to account its SEUs when deciding and establishing the objectives and energy targets. It would make sense that some of the objectives and energy targets are specifically aimed at improvements for specific SEUs.
| 2 | PLAN | 8, 9 | 6.3 Energy review | The organization shall develop and conduct an energy review. To develop the energy review, the organization shall: a) …. b) based on the analysis, identify SEUs (see 3.5.6); c) for each SEU: 1) determine relevant variables; 2) determine current performance; 3) identify the person(s) doing work under its control that influence or affect the SEUs; | The plant energy review and energy balance will help to find the SEUs. All energy sources must be considered. SEUs can be facilities, systems, processes, or equipment. Relevant variables are things like production volume, cooling degree days, heating degrees days, etc. You must know how much energy your SEUs are consuming down to the equipment level and you must estimate future energy use and consumption for all SEUs. You must know who is working with your SEUs.
| 3 | PLAN | 8 | 6.6 Planning for collection of energy data | Data to be collected (or acquired by measurement as applicable) and retained documented information (see 7.5) shall include: a) the relevant variables for SEUs; b) energy consumption related to SEUs and to the organization; c) operational criteria related to SEUs; | You must determine relevant variables such as production volume, cooling degree days, heating degrees days, etc., for all SEUs. You must collect and retain consumption data on all SEUs. You must intergrate your SEUs with you operational and maintenance criteria.
| 4 | DO | 17 | 8.1 Operational planning and control | The organization shall plan, implement and control the processes, related to its SEUs (see 6.3), needed to meet requirements and to implement the actions determined in 6.2, by: a) establishing criteria for the processes, including the effective operation and maintenance of facilities, equipment, systems and energy-using processes, where their absence can lead to a significant deviation from intended energy performance; b) communicating (see 7.4) the criteria to relevant person(s) doing work under the control of the organization; c) implementing control of the processes in accordance with the criteria, including operating and maintaining facilities, equipment, systems and energy-using processes in accordance with established criteria; d) keeping documented information (see 7.5) to the extent necessary to have confidence that the processes have been carried out as planned. The organization shall control planned changes and review the consequences of unintended changes, taking actions to mitigate any adverse effects, as necessary. The organization shall ensure that outsourced SEUs or processes related to its SEUs (see 6.3) are controlled (see 8.3). | Operational and maintenance controls, activities and criteria are centered around your selected SEUs. Absence of these controls could lead to problems with the performance of the SEUs. This must be monitored and tracked, and records kept. Significant deviations must be defined. Once the criteria and activities are set up, they must be followed. You must inform, train, or make aware all relevant person(s) who carry out these controls on the SEUs. Documented information must be maintained on the above actions. The above includes outsourced SEUs and processes related to SEUs.
| 5 | DO | 19 | 8.3 Procurement | When procuring energy using products, equipment and services that have, or can have, an impact on SEUs, the organization shall inform suppliers that energy performance is one of the evaluation criteria for procurement. | You must inform suppliers that energy performance is part of the procurement evaluation process for anything that is purchased that can have an impact on an SEU. This can take the form of a letter or an email to selected suppliers. Records of this action should be maintained as evidence of completion.
| 6 | CHECK | 20, 21 | 9.1 Monitoring, measurement, analysis and evaluation of energy performance and the EnMS | 9.1.1 General The organization shall determine for energy performance and the EnMS: a) what needs to be monitored and measured, including at a minimum the following key characteristics: 1) 2) 3) operation of SEUs; 4) | The operation of SEUs must be part of the overall monitoring plan for the organization. The methods for monitoring, measuring, analyzing and evaluating data related to SEUs must be determined. When monitoring and measurement of data related to SEUs occurs must be determined. When analysis and evaluation of data related to SEUs occurs must be determined. Results of the above actions must be part of the organization's documented information.

## 8_Energy IMPV
8 | DTNA Site: | [5 empty] | From ISO 50001 | 6.3 Energy review
|  | Energy Improvement Project Evaluation | [5 empty] | The organization shall develop and conduct an energy review.
|  | List and Rank Energy Improvement Projects based on SEUs and other factors | [5 empty] | To develop the energy review, the organization shall:
|  | Use SEU pie chart and other inputs for generating ideas for energy improvements | [5 empty] | a), b), c), …..
d) determine and prioritize opportunities for improving energy performance;
[21 empty] | EVALUATION CRITERIA and SCORING (5 = BEST) | [5 empty] | Criteria Scoring Details BELOW** |  |  | Pull Down Menu | Pull Down Menu | FOLLOW UP
| Project ID# | Performance Improvement Opportunity Name | Performance Improvement Opportunity Description | Related to a Significant Energy User (SEU)? Which One? | Part of Energy Target (Enter Name) - Optional | Responsible Lead Person (Name) | Date Entered | Estimated Annual Savings (should have back up calculation available) | [7 empty] | Non-Energy Benefits (list name and estimated value, if known) |  |  |  | Estimated Project Cost | 1. Project COST | 2. Simple Payback | 3. Implementation Time | 4. Non-Energy Benefits | 5. Plant Employee Impact | 6. Add OTHER | 7. Add OTHER | 8. Add OTHER | Opportunity Score (multiply) | Prioritization Level | Implementation Status | Project Completion Date | Actual Annual Savings | [7 empty] | Actual Non-Energy Benefits Realized |  |  |  | Actual Implementation Cost
[8 empty] | Electricity (kWh) | Natural Gas (therms) | Liquid Propane (gallons) | Diesel Fuel (gallons) | Other Fuel Oils (gallons) | Other | Other | Other | 1 | 2 | 3 | 4 |  | Lower = 5 Higher = 1 | Lower = 5 Higher = 1 | Shorter = 5 Longer = 1 | More = 5 Less = 1 | Higher = 5 Lower = 1 | Best= 5 Worst= 1 | Best= 5 Worst= 1 | Best= 5 Worst= 1 |  |  |  |  | Electricity (kWh) | Natural Gas (therms) | Liquid Propane (gallons) | Diesel Fuel (gallons) | Other Fuel Oils (gallons) | Other | Other | Other | 1 | 2 | 3 | 4
EXAMPLE | EEM# 29 | Chilled Water Pump VFDs | Add VFDs and controls to the chilled water primary supply pump motors, eight motors at 50 hp each | YES, Chillers | Improve Overall HVAC Energy Consumption | M. Stowe | 2020-04-21 | 475000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Reduce chiller condenser water make up by ~ 15% | Improve consistency of plant air temperature and humidity |  |  | 17500 | 4 | 5 | 3 | 1 | 3 | x | x | x | 180 | High | Completed | 2020-07-12 | TBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Reduced chiller condenser water make up by ~ 18% | Improved consistency of plant air temperature and humidity |  |  | 16785
0
0
0
0
0
0
0
**Scoring Criteria Details
[21 empty] | 1. Project COST ($) |  |  | 5. Plant Employee Impact |  | Empolyee Impact Definitions
[21 empty] | $5,000 or less | 5 |  | Significant | 5 | Significant | Good | Some | Limited | No Impact
[21 empty] | > $5,000 up to $50,000 | 4 |  | Good | 4 | Employees have a direct and substantial impact on the successful implementation of the energy project | Employees still have a direct, but less substantial impact on the successful implementation of the energy project | Employees still have some, but a much less substantial impact on the successful implementation of the energy project | Employees have limited impact on energy project success because the new system is mostly automated and needs very little human interface | The energy project deploys a fully automated systems with very little to no human interface.
[21 empty] | > $50,000 up to $500,000 | 3 |  | Some | 3
[21 empty] | > $500,000 up to $1,000000 | 2 |  | Limited | 2
[21 empty] | > $1,000,000 | 1 |  | No impact | 1
[21 empty] | 2. Simple Payback (years) |  |  |  |  | Project EXAMPLES: Compressed air leak repair Equipment start up and shut down optimization Behaviorial based projects like turning off lights and computers | Project EXAMPLES: Installing an automated control system where employees still have a good amount of input Implementing condenser water reset for chillers | Project EXAMPLES: Installing VFDs on pump and fan motors that will general operate automatically, but still require set up, system operation, and periodic adjustments by technicians | Project EXAMPLES: Installing a VFD air compressor that automatically starts and loads up and down based on plant air pressure | Project EXAMPLES: Installing a fully automated building control system that, once set up, pretty much runs on its own
[21 empty] | 2 years or less | 5
[21 empty] | > 2 up to 3 years | 4
[21 empty] | > 3 up to 4 years | 3
[21 empty] | > 4 up to 5 years | 2
[21 empty] | > 5 years | 1
3. Implementation Time (years)
[21 empty] | 6 months or less | 5 |  | Add Others
[21 empty] | > 6 month up to 1 year | 4 |  |  | 5
[21 empty] | > 1 year up to 3 years | 3 |  |  | 4
[21 empty] | > 3 years up to 5 years | 2 |  |  | 3
[21 empty] | > 5 years | 1 |  |  | 2
1
4. Non-Energy Benefits
[20 empty] | From the list below: | > 4 | 5
[21 empty] | Up to 4 | 4
[21 empty] | Up to 3 | 3
[21 empty] | Up to 2 | 2
[21 empty] | NONE | 1
NON-Energy Benfits List
Productivity improvements
Quality improvements
Ergonomic improvements
Better material flow
Labor savings
Scrap reduction
Reduce overtime
Water use reduction
Waste reduction
Emissions reduction
Pollution reduction
Permitting requirements reduced
Employee work condition improvements
Operational safety improvements
Better floor space utilization
Carbon footprint reduction
Greenhouse gas reduction
Public relations improved
Brand enhancement
Please add more, as needed
Note on X7: Author: Include potential equipment repair expenses here, as needed.
Note on Y7: Author: Include potential equipment repair expenses here, as needed.
Note on AA7: Author: Refer to non energy benefits section of this tab at columns "S" thru "V" and the table below
Note on AF7: Author: Formula is currently set up to multiply the first FIVE scores. If you add criteria 6, 7, or 8, than add these to the formula. Also, if desired, you can make this a weighted formula, e.g. to give say, cost a 50% weighting, etc.

## 9_Action Plan Template
9 |  | DTNA Site: | [8 empty] | From ISO 50001 | 6.2.3 When planning how to achieve its objectives and energy targets, the organization shall establish and maintain action plans that include:
|  |  | Action Plan Template | [9 empty] | — what will be done;
|  |  | Use the template below to develop action plans for energy improvement projects from Tab 8. | [9 empty] | — what resources will be required;
— who will be responsible;
— when it will be completed;
— how the results will be evaluated, including the method(s) used to verify energy performance improvement (see 9.1).
Energy Management Action Plan Template (print out, fill out, and retain) | [11 empty] | The organization shall consider how the actions to achieve its objectives and energy targets can be integrated into the organization’s business processes. The organization shall retain documented information on action plans (see 7.5).
| Project Objective/Target: | [15 empty] | Planned Completion Date:
Actual Completion Date:
Project Description:
| Project Budget: | [7 empty] | Project Leader:
| Actual Cost: | [7 empty] | Management Review:
Project Planning
| Action Items | [5 empty] | Leader Position |  |  |  | Due Date |  |  | Completion Date |  | Required Resources/Comments
Project Results Verification
Describe the method(s) to be used to verify the results of the action plan and the energy performance improvement achieved:
| Unit(s) of Measurement |  |  |  | Pre-Project Value | Post Project Value |  | Net Change |  | Source of Measurement | [7 empty] | Date Done | Responsible Party
(e.g. meter ID, calculation formula, etc.)
Evaluation of Results:
Communication/Training Plan: Identify departments affected by the project. 1) Mark the first column for departments involved with/affected with the project implementation with a capital "I" 2) Mark the second column for departments involved with/affected by sustaining the project improvements with a capital "S"
| All Departments |  |  |  |  | Production | [8 empty] | Lab
| Sales/Marketing |  |  |  |  | Maintenance | [8 empty] | Purchasing
| Accounting |  |  |  |  | Transportation | [8 empty] | Bldg./Facility Ops & Mgt
| Human Resources |  |  |  |  | Warehouse | [8 empty] | Corporate
| Customer Service |  |  |  |  | Custodial/Housekeeping | [8 empty] | Contractors
Sustaining the project improvements
Document the details for each responsibility necessary to sustain the energy savings achieved by the project’s implementation.
| Item |  | Leader Position | What needs to be done?, i.e. tasks/assignments for this item
Roles
Resources
Communication
Training
Oper. Controls
Monitoring & Measurement
Process Changes
Project Follow-up Notes/Lessons Learned

## 10_Operational Controls
10 |  | DTNA Site: |  |  |  | From ISO 50001 | 8.1 Operational planning and control
|  | Operation Controls Planning Template |  |  |  |  | The organization shall plan, implement and control the processes, related to its SEUs, needed to meet requirements, and to implement the action plans by:
a) establishing criteria for the processes, including the effective operation and maintenance of facilities, equipment, systems and energy-using processes, where their absence can lead to a significant deviation from intended energy performance;
|  |  | EXAMPLE | [5 empty] | NOTE: Significant deviation criteria are determined by the organization.
b) communicating the criteria to relevant person(s) doing work under the control of the organization;
c) implementing control of the processes in accordance with the criteria, including operating and maintaining facilities, equipment, systems and energy-using processes in accordance with established criteria;
d) keeping documented information (see 7.5) to the extent necessary to have confidence that the processes have been carried out as planned.
The organization shall control planned changes and review the consequences of unintended changes, taking actions to mitigate any adverse effects, as necessary.
The organization shall ensure that outsourced SEUs or processes related to its SEUs are controlled (see 8.3).
| DTNA Operational & Maintenance Controls Planning Worksheet | [25 empty] | NOTE: Once the Operational controls and maintenance criteria are identified, they must be communicated to the appropriate personnel and implemented
|  | USE for both SEUs and/or Action Plans (APs) | [13 empty] | UCL = Upper Control Limit |  |  |  |  | Focus on biggest energy
SEU or AP # |  | Short Name | [14 empty] | LCL = Lower Control Limit |  |  |  | consumers FIRST
SEU #1 |  | COOLING | Associated with this SEU |  |  |  | Energy Types Consumed by this SEU | BRAINSTORM Operational Controls |  |  | Identify Additional Information for Selected Parameters | [7 empty] | Parameter Monitoring | [5 empty] | Identify Maintenance Criteria |  | Communicate to the Appropriate Personnel |  |  |  |  | Implement the Selected Operational Controls and Maintenance Criteria |  |  |  | Process for Managing Changes
|  | Full Description | Facilities | Processes | Systems | Equipment |  |  |  |  | Parameter | Instrument | Calibration Required? | Units | Value | UCL | LCL | Energy Impact Trend | WHO? | WHAT? | WHERE? | WHEN? | HOW? | Action for Data | Describe the maintenance system for the SEU system including who, what, where, when, and how: |  | Role |  | Group | X | Methods (mark all used) | Decide on Implementation Tools |  | X | Implementation Tools (mark all used)
|  | Building Cooling | Central Energy Plants | Vapor compression | Chilled Water | Chillers-Water cooled | Electricity | What system parameters can impact the energy consumption of this SEU/Action Plan? (list) |  |  | Chilled water return temperature | Temperature Gauge | YES | ◦F | 55 | 59 | 51 | Higher indicates more cooling load | DPW O&M Techs | Temperatures | Central Energy Plants | Temperatures: Hourly | Log sheets | Send log sheets and data downloads to the Energy Team Leader at DPW. The Energy Team Leader and REMs will review and analyze the data, and give feedback on any action needed to the O&M teams. | All equipment related to the COOLING SEU is properly maintained per manufacturer's recommendations using the XYZ Maintenance Management System. PM work orders are issued based on the periodicity of the PM item and PMs are then scheduled and completed. Records of completed PMs are maintained by DPW. ....AND SO ON... |  | Equipment Operators |  | DPW | X | Shift or toolbox meetings | 1) For each selected implementation tool: |  |  | Work instructions | 1) BRAINSTORM with the Team:
|  | Equipment Cooling | Individual Buildings | Thermodynamics | Condenser Water | Chiller Compressors |  | Chilled water return temperature |  | Chiller sequencing program | Chilled water supply temperature | Temperature Gauge | YES | ◦F | 45 | 47 | 43 | Lower takes more energy to create | Honeywell Operators | T-Stat Setpoints | Individual Buildings | T-Stat Setpoints: | Building automation sys. | [5 empty] | Honeywell | X | Demonstrations |  | a) Create the tool, if needed | X | Standard Operating Procedures (SOPs) |  | a) What unplanned changes could occur to impact this SEU energy performance:
|  |  | Data Centers | Pumping | HVAC | Chilled Water Pumps |  | Chilled water supply temperature |  | Building automation setpoints | Condenser water supply temperature | Temperature Gauge | YES | ◦F | 65 | 78 | 65 | Cooler makes the chiller more efficient | Facility Managers |  | Commands | Periodically (TBD) | [6 empty] | JCI |  | E-mails |  | b) Include the tool in document control, as needed | X | Log sheets |  |  | Examples:
|  |  | Dining Facilities |  | (Ventilation) | Condenser Water Pumps |  | Condenser water supply temperature |  | Air handling unit outside air dampers | Thermostat settings | Variety of Thermostats |  | ◦F | 74 | n/a | n/a | Lower setting will require more cooling | Building Energy Managers |  | Barracks | [9 empty] | Staff meetings |  | c) Train personnel on how to use the tool |  | Logbooks |  |  | Random people adjusting thermostats
|  |  | Commissaries |  | (Air Conditioning) | Cooling Towers |  | Thermostat settings |  | Chiller loading / unloading (i.e. cycling) | etc. | [7 empty] | Others |  | Dining Facilities | 24 x 7 |  |  |  |  | Maintenance Technicians |  | DPW | X | Equipment markings |  | d) Start using the tool |  | Checklist |  |  | Setpoints on equipment changed without approval
[5 empty] | Humidity Control | Cooling Tower Fans |  | Control valve positions |  | Heating and cooling at the same time | OTHERS? | [9 empty] | Others | [7 empty] | Honeywell |  | Supplier meetings |  | e) Collect data from the tool | X | Work area postings |  |  | Some function bypassed
[5 empty] | Controls | Chillers-Air cooled |  | VFD settings | [20 empty] | JCI | X | Contractor briefings |  | f) Follow up to make sure the tool is effective | X | Signs and labeling |  | b) How can these be avoided | VFD setting changed
[5 empty] | Instrumentation | Other pumps |  | Which of these parameters can be readily monitored, measured, and controlled? (list) | [21 empty] | X | On-the-job training |  | g) Follow up to make sure the tool is being used properly |  | Specific personnel certifications |  |  | Not completing a required PM item
[5 empty] | Two-Pipe Systems | Other Fans | [20 empty] | Building Managers |  | DPW | X | Shift training |  | h) Periodically review and update tools |  | Brochures and other visual aids |  |  | Removing a critical sensor
[5 empty] | Four-Pipe Systems | Air Handling Units | [22 empty] | Bragg Site | X | Classroom training |  |  |  | Templates
[6 empty] | Cooling Coils | [19 empty] | Typical maintenance items include: |  |  | Commands |  | Supplier training |  |  | X | Statistical Process Control (SPC) charts | 2) When changes are required:
[6 empty] | Control Valves | [19 empty] | Lubrication |  |  |  | X | Peer mentoring |  |  | X | Building automation systems |  | a) Document the change
[6 empty] | Heat Exchangers | [19 empty] | Filter replacement | Operational and Maintenance |  |  |  | On-line training |  |  |  | Spreadsheets |  | b) Communicate the change to appropriate personnel
[6 empty] | VFDs | [19 empty] | Tension adjustment |  | Leaders | DPW |  | Training from certified bodies | [5 empty] | c) Update implementation tools, as needed
[8 empty] | Selected parameters for this SEU/Action Plan (list) | [17 empty] | Cleaning |  |  | Honeywell | X | Technical training | [5 empty] | d) Follow up to ensure that the change is effective and working well
[26 empty] | Leak repair |  |  | JCI
Fluid levels
[26 empty] | Thermography | Others:
Vibration analysis
[16 empty] | UCL = Upper Control Limit | [9 empty] | Tuning, etc. |  |  |  |  | ADD OTHERS, as needed |  |  |  | ADD OTHERS, as needed
SEU or AP # |  | Short Name | [14 empty] | LCL = Lower Control Limit
SEU #2 |  | HEATING | Associated with this SEU |  |  |  | Energy Types Consumed by this SEU | BRAINSTORM Operational Controls |  |  | Identify Additional Information for Selected Parameters | [7 empty] | Parameter Monitoring | [5 empty] | Identify Maintenance Criteria |  | Communicate to the Appropriate Personnel |  |  |  |  | Implement the Selected Operational Controls and Maintenance Criteria |  |  |  | Process for Managing Changes
|  | Full Description | Facilities | Processes | Systems | Equipment |  |  |  |  | Parameter | Instrument | Calibration Required? | Units | Value | UCL | LCL | Energy Impact Trend | WHO? | WHAT? | WHERE? | WHEN? | HOW? | Action for Data | Describe the maintenance system for the SEU system including who, what, where, when, and how: |  | Role |  | Group | X | Methods (mark all used) | Decide on Implementation Tools |  | X | Implementation Tools (mark all used)
|  | Building Heating | Central Energy Plants | Combustion | MTHW | Boilers | Electricity | What system parameters can impact the energy consumption of this SEU/Action Plan? (list) | [22 empty] | Shift or toolbox meetings | 1) For each selected implementation tool: |  |  | Work instructions | 1) BRAINSTORM with the Team:
|  | Water Heating | Individual Buildings | Thermodynamics | LTHW | Combustion Burners | Natural Gas | MTHW supply temperature |  | Combustion burner settings | [20 empty] | Demonstrations |  | a) Create the tool, if needed |  | Standard Operating Procedures (SOPs) |  | a) What unplanned changes could occur to impact this SEU energy performance:
|  |  | Barracks | Pumping | HVAC | Combustion Blowers | #2 Fuel Oil | LTHW supply temperature |  | Flue exhaust oxygen level | [20 empty] | E-mails |  | b) Include the tool in document control, as needed |  | Log sheets |  |  | Examples:
|  |  | Dining Facilities |  | (Heating) | Hot Water Pumps |  | Thermostat settings |  | Percent excess air to burners | [20 empty] | Staff meetings |  | c) Train personnel on how to use the tool |  | Logbooks |  |  | Random people adjusting thermostats
[5 empty] | Controls | Feed Water Pumps |  | Control valve positions |  | Boiler loading / loading (i.e. cycling) | [20 empty] | Equipment markings |  | d) Start using the tool |  | Checklist |  |  | Setpoints on equipment changed without approval
[5 empty] | Instrumentation | Fans |  | VFD settings |  | Heating and cooling at the same time | [20 empty] | Supplier meetings |  | e) Collect data from the tool |  | Work area postings |  |  | Some function bypassed
[5 empty] | Two-Pipe Systems | Other Pumps | [24 empty] | Contractor briefings |  | f) Follow up to make sure the tool is effective |  | Signs and labeling |  | b) How can these be avoided | VFD setting changed
[5 empty] | Four-Pipe Systems | Direct Fired Heating |  | Which of these parameters can be readily monitored, measured, and controlled? (list) | [22 empty] | On-the-job training |  | g) Follow up to make sure the tool is being used properly |  | Specific personnel certifications |  |  | Not completing a required PM item
[6 empty] | Air Handling Units | [24 empty] | Shift training |  | h) Periodically review and update tools |  | Brochures and other visual aids |  |  | Removing a critical sensor
[6 empty] | Heating Coils | [24 empty] | Classroom training |  |  |  | Templates
[6 empty] | Heat Exchangers | [19 empty] | Typical maintenance items include: |  |  |  |  | Supplier training |  |  |  | Statistical Process Control (SPC) charts | 2) When changes are required:
[6 empty] | Control Valves | [19 empty] | Lubrication |  |  |  |  | Peer mentoring |  |  |  | Building automation systems |  | a) Document the change
[6 empty] | VFDs | [19 empty] | Filter replacement |  |  |  |  | On-line training |  |  |  | Spreadsheets |  | b) Communicate the change to appropriate personnel
[26 empty] | Tension adjustment |  |  |  |  | Training from certified bodies | [5 empty] | c) Update implementation tools, as needed
[8 empty] | Selected parameters for this SEU/Action Plan (list) | [17 empty] | Cleaning |  |  |  |  | Technical training | [5 empty] | d) Follow up to ensure that the change is effective and working well
Leak repair
Fluid levels
Thermography
Vibration analysis
[16 empty] | UCL = Upper Control Limit | [9 empty] | Tuning, etc. |  |  |  |  | ADD OTHERS, as needed |  |  |  | ADD OTHERS, as needed
SEU or AP # |  | Short Name | [14 empty] | LCL = Lower Control Limit
SEU #3 |  | LIGHTING | Associated with this SEU |  |  |  | Energy Types Consumed by this SEU | BRAINSTORM Operational Controls |  |  | Identify Additional Information for Selected Parameters | [7 empty] | Parameter Monitoring | [5 empty] | Identify Maintenance Criteria |  | Communicate to the Appropriate Personnel |  |  |  |  | Implement the Selected Operational Controls and Maintenance Criteria |  |  |  | Process for Managing Changes
|  | Full Description | Facilities | Processes | Systems | Equipment |  |  |  |  | Parameter | Instrument | Calibration Required? | Units | Value | UCL | LCL | Energy Impact Trend | WHO? | WHAT? | WHERE? | WHEN? | HOW? | Action for Data | Describe the maintenance system for the SEU system including who, what, where, when, and how: |  | Role |  | Group | X | Methods (mark all used) | Decide on Implementation Tools |  | X | Implementation Tools (mark all used)
|  | Site-wide | All buildings on site | Illumination | Lighting circuits | Fixtures | Electricity | What system parameters can impact the energy consumption of this SEU/Action Plan? (list) | [22 empty] | Shift or toolbox meetings | 1) For each selected implementation tool: |  |  | Work instructions | 1) BRAINSTORM with the Team:
|  | Indoor |  |  | Controls | Lamps |  | Time that the lights are on, especially when not needed | [22 empty] | Demonstrations |  | a) Create the tool, if needed |  | Standard Operating Procedures (SOPs) |  | a) What unplanned changes could occur to impact this SEU energy performance:
|  | Outdoor |  |  |  | Occupancy Sensors |  | Proper operation of occupancy and daylight sensors | [22 empty] | E-mails |  | b) Include the tool in document control, as needed |  | Log sheets |  |  | Examples:
[6 empty] | Timers | [24 empty] | Staff meetings |  | c) Train personnel on how to use the tool |  | Logbooks |  |  | Random people adjusting thermostats
[6 empty] | Daylight Sensors | [24 empty] | Equipment markings |  | d) Start using the tool |  | Checklist |  |  | Setpoints on equipment changed without approval
[31 empty] | Supplier meetings |  | e) Collect data from the tool |  | Work area postings |  |  | Some function bypassed
[31 empty] | Contractor briefings |  | f) Follow up to make sure the tool is effective |  | Signs and labeling |  | b) How can these be avoided | VFD setting changed
[8 empty] | Which of these parameters can be readily monitored, measured, and controlled? (list) | [22 empty] | On-the-job training |  | g) Follow up to make sure the tool is being used properly |  | Specific personnel certifications |  |  | Not completing a required PM item
[31 empty] | Shift training |  | h) Periodically review and update tools |  | Brochures and other visual aids |  |  | Removing a critical sensor
[31 empty] | Classroom training |  |  |  | Templates
[26 empty] | Typical maintenance items include: |  |  |  |  | Supplier training |  |  |  | Statistical Process Control (SPC) charts | 2) When changes are required:
[26 empty] | Lubrication |  |  |  |  | Peer mentoring |  |  |  | Building automation systems |  | a) Document the change
[26 empty] | Filter replacement |  |  |  |  | On-line training |  |  |  | Spreadsheets |  | b) Communicate the change to appropriate personnel
[26 empty] | Tension adjustment |  |  |  |  | Training from certified bodies | [5 empty] | c) Update implementation tools, as needed
[8 empty] | Selected parameters for this SEU/Action Plan (list) | [17 empty] | Cleaning |  |  |  |  | Technical training | [5 empty] | d) Follow up to ensure that the change is effective and working well
Leak repair
Fluid levels
Thermography
Vibration analysis
[26 empty] | Tuning, etc. |  |  |  |  | ADD OTHERS, as needed |  |  |  | ADD OTHERS, as needed
NOTE:
Work through this brainstorming exercise with your DPW O&M teams and contractors, especially Honeywell and SELECT your parameters for every SEU.
NOTE:
Operational controls establish criteria to monitor to optimize the energy performance of an SEU. The absence of these operational control parameters can lead to a significant deviations from intended energy performance.
Imagine how chiller energy consumption would be impacted if there were no controls on thermostats!
NOTE:
Examples of significant deviation include:
Systems running outside of control limits
Energy consumption varies unexpectedly
Change in efficiency
Increased maintenance requirements
Increased equipment downtime
Increased in equipment load time
Longer run times
Need to change settings frequently
NOTE:
Possible sources for finding operational control criteria:
Manufacturer’s recommendation
Equipment technical manuals
Subject Matter Experts
Minimum process or system requirements
Service personnel suggested operating settings
Statistical process controls
Benchmarking performance of similar equipment
Industry standards
NOTE:
This section identifies details on the process for monitoring the selected parameters:
WHO? = Who monitors the parameter and collects information?
WHAT? = What specific information is collected?
WHERE? = Where on site, within the scope of the EnMS are systems located that need the monitoring?
WHEN? = When is data collected and recorded?
HOW? = How is the data collected? Is this a manual pen & paper process or is this information recorded in a building automation system, etc.
Action for data: Once the data is collected, what is done with it. Where is the data stored? Who gets the data? Who aggregates the data Who analyzes the data? Who issues actions based on the data analysis?
NOTE:
In addition to the operational controls, SEUs must also receive proper maintenance. This should already be in place for the SEU equipment. For the EnMS there must be specific maintenance criteria in the form of a preventative maintenance system (PMS) with daily, weekly, monthly, annual, etc. periodic maintenance items to be competed on the SEU systems. Records of the scheduling and completion of these PMS items must be kept.
NOTE:
Once identified, it is very important to communicate these selected operational controls and maintenance criteria to the appropriate personnel.
Appropriate personnel should include operators and maintenance technicians for the equipment and systems designated as SEUs. This must include site personnel and contractors. Leadership for these personnel should also be in the loop for this.
Communications should include the operational controls and maintenance criteria identified in the previous columns of the planning worksheet, or basically who, what, when, where, how, how often, records, documentation, and response to signification deviations.
Any forms, log sheets, building automation systems, etc., that will be used should be included in these communications.
NOTE:
Closely tied to the communication of operational controls and maintenance criteria are the implementation tools.
The energy team and the equipment operators, maintenance techs, and others should work together to develop and issue the forms, log sheets, building automation systems, etc., that will be used for monitoring and completing operational controls and maintenance criteria.
NOTE:
The key point here are:
- Anticipate unplanned changes that may occur and avoid these
- Train personnel NOT to randomly change critical operational control parameters without approval
- When changes are needed, follow the process for completing the change

## 99A_Baseline&Achievement
99A
Baseline and Achievement Period Examples for Energy Improvement
Reference Info
Relationship between
|  |  | Baseline Period |  |  | Must be at least 12 months long
|  |  | Achievement Period |  |  | Starts at the end of the Baseline Period and must be at least 12 months long, but no more that 120 months long
|  |  | Reporting Period |  |  | Must be at least 12 months long
Achievement Period and Reporting Period must END at the same time
Achievement Period does NOT have to be a multiple of 12 months, although this is convenient
Examples:
|  | #1 | Shortest Possible Scenario
|  | Baseline Period | 12 | months
|  | Achievement Period | 12 | months
|  | Reporting Period | 12 | months
Reporting Period
| Baseline Period |  |  |  | Achievement Period
| 2014-01-01 |  |  |  | 2015-01-01 |  |  | 2016-01-01
|  | #2 | Typical Scenario
|  | Baseline Period | 12 | months
|  | Achievement Period | 36 | months
|  | Reporting Period | 12 | months
Reporting Period
| Baseline Period |  |  |  | Achievement Period
| 2014-01-01 |  |  |  | 2015-01-01 |  |  | 2016-01-01 |  | 2017-01-01 |  | 2018-01-01
|  | #3 | Longest Possible Scenario
|  | Baseline Period | 12 | months
|  | Achievement Period | 120 | months
|  | Reporting Period | 12 | months
Reporting Period
| Baseline Period |  | Achievement Period
| 2014-01-01 |  | 2015-01-01 |  | 2016-01-01 |  | 2017-01-01 | 2018-01-01 | 2019-01-01 | 2020-01-01 | 2021-01-01 | 2022-01-01 | 2023-01-01 | 2024-01-01 | 2025-01-01

## 99B_Bottom Up Graphic
99B
Bottom Up Energy Savings Example Graphic
Reference Info
| Top-Down Energy Savings, using the model | [6 empty] | Bottom-Up Energy Savings, using the Registry
Project 6
TD Total Energy Savings
|  |  | Total Energy Used (THEN) |  |  | ESPTD
[7 empty] | Should be close |  |  |  | Project 5
Project 4
BU Total Energy Savings
[9 empty] | ESPBU |  | Project 3
Project 2
Total Energy Used (NOW)
Project 1
RF = ESPBU / ESPTD