## 1_INTRO
1 | Energy Mapping Process for ANY SITE
Reference Info
Introduction
From ISO 50001: 2018 Annex A, section A.6, Planning

## 2_Energy IN & OUT
2 |  |  | Energy Mapping Process for ANY SITE
ANY SITE
Energy Types INTO and OUT OF the Site Boundaries
Energy Types INTO the SITE | [7 empty] | Convert to Primary** | [5 empty] | Site Boundary | [12 empty] | **Convert to Primary (if required) | Energy Types OUT of the SITE
| Y | Feedstocks | [25 empty] | Y | Pass Through = unused input energy (e.g. fuel loaded into trucks or buses)
|  | N | Liquid Propane (LP) fuel
|  | N | Diesel fuel | [24 empty] | Y | Non Energy Product, e.g. pure water, bricks, cars, paper, cloth, tires, etc.
|  | N | Other fuels, not consumed on site
| Y | Primary | [25 empty] | N | Energy Product |  |  | Energy product sold must be considered as a relevant variable in the model
|  | Y | Natural Gas | [25 empty] | N | Product Sold containing Energy Content, e.g. gasoline, kerosene, etc.
|  | Y | Liquid Propane (LP) | [5 empty] | On Site Storage | [19 empty] | N | Excess Energy greater than the Energy from an Outside Source (by energy type)
|  | Y | Diesel (consumed on site) | [6 empty] | Diesel Fuel |  |  |  |  | Office Buildings | [14 empty] | N | Grid Delivered Electricity |  | An Energy Product is converted to primary energy using the same multiplier as the energy type that was generated or extracted on-site within the facility boundaries
|  | N | Coal | [6 empty] | Fuel Oil |  | Data Centers |  |  |  | HVAC Loads | [13 empty] | N | Steam
|  | N | Other Fuel Oils | [6 empty] | LP Gas |  |  | Server Load |  |  | Lighting Loads |  |  |  |  | Production Buildings/Warehouses | [8 empty] | N | Hot Water
| Y | Derived | [7 empty] | Other |  |  | Cooling Load | [8 empty] | Forming, Fabrication, Assembly, Machining | [7 empty] | N | Chilled Water
|  | Y | Grid Delivered Electricity | [18 empty] | Welding, Heat Treatment, Washing, Drying | [7 empty] | N | Compressed Air
|  | N | Steam | [18 empty] | Coating, Painting, Curing, Lighting, Testing | [5 empty] | N | Energy Export
|  | N | Hot Water | [19 empty] | Ventilation, Air Handlers, Exhaust | [5 empty] | Y | Energy SENT to the Outside less than or equal to the Energy from an Outside source (by energy type)
|  | N | Chilled Water | [19 empty] | Process Water & Make-up Air Heating | [6 empty] | Y | Grid Delivered Electricity |  | An Energy Export is converted to primary energy using the same multiplier as the energy type that was delivered to the facility boundaries
|  | N | Compressed Air | [6 empty] | Other Buildings | [7 empty] | Facility Buildings/Rooms | [11 empty] | N | Steam
|  | N | Solar Electricity | [7 empty] | Training Facilities |  | Thermal Storage | [5 empty] | Air Compressors, Boilers, Pumping | [10 empty] | N | Hot Water
|  | N | Wind Electricity | [7 empty] | Dining Facilities |  |  | Chilled water |  |  |  |  | Chillers & Cooling Towers | [10 empty] | N | Chilled Water
|  | N | Geothermal Electricity | [7 empty] | Labs, etc. | [7 empty] | HVAC, Wastewater Treatment, etc. | [10 empty] | N | Compressed Air
|  | N | Solar/Geo Steam | [20 empty] | Other
|  | N | Still Gas | [5 empty] | Primary Energy Sources from | [6 empty] | On Site Generation
|  | N | Various Biomass | [5 empty] | INSIDE the boundaries (extraction) | [15 empty] | Solar Panels |  |  |  | CHP Residuals (electricity, steam)
|  |  | N | Agriculture Residue (Hog Waste) | [5 empty] | N | Oil well | [18 empty] | Do not drive energy consumption
|  |  | N | Herbaceous Crops | [5 empty] | N | Natural gas well | [18 empty] | Not included in the energy model
|  |  | N | Woody Crops | [5 empty] | N | Biogas from onsite landfill |  |  |  |  | Combined Heat & Power | [5 empty] | Backup Generators
|  |  | N | Forest Residues | [5 empty] | Y | Renewables on site: solar, wind, etc. | [5 empty] | Electricity | [5 empty] | Diesel | [5 empty] | CHP specifically to sell (electricity, steam)
|  |  | N | Wastewater Sludge | [5 empty] | N | Others | [5 empty] | Steam | [5 empty] | Natural Gas | [6 empty] | Considered a generation product
|  |  | N | Food Scraps (RCI*) | [25 empty] | Must be considered for the energy model
|  |  | N | Other Biogas/Biomass/Biofuel |  |  | **Use Conversion Factors and Multipliers, if using primary energy | [12 empty] | Site Boundary | [5 empty] | **Use Conversion Factors and Multipliers, if using primary energy
These items must be included in the energy accounting:
| *RCI = Restaurants, Cafeterias and Institutions | [8 empty] | Energy producing processes
Exothermic reactions, etc.

## 3A_Energy CONSUMED
3A |  |  | Energy Mapping Process for ANY SITE
Reference Info
Energy CONSUMED within the Site Boundaries
Where does all the energy go?
GOAL: Using the input and outputs from Step 1, determine where all the energy goes within the site boundaries
| METHODS: | [13 empty] | Main Gas Utility Meter | [6 empty] | Gas Meter on a Boiler
|  | Natural Gas: | [5 empty] | Therms/DekaTherms/MMBTU
|  |  | Main utility meter | [6 empty] | CUFT
Sub-meters on equipment
Typically much lower number of end users
Typically well known primary users:
Boilers
Hot water
Process heating
The "H" in HVAC
|  | Electricity: | [5 empty] | kWh
TOP DOWN:
Track the electricity from the utility substation to the end electrical user
[5 empty] | Electrical utility feeders and substations | [14 empty] | One-Line Electrical Drawings | [6 empty] | Motors Control Centers (MCCs)
Main utility meter
Site one-line electrical diagram for distribution
Site substations
[6 empty] | Distribution panels | [5 empty] | Arc Flash Studies
Motor control centers
Busess ducts
Breaker Panels
Local Disconnects
Sub-meters on equipment
Permanent
Temporary
[6 empty] | Electrical End Uses: |  |  |  |  | LOTS & LOTS
Motors, typically the largest
Resistance Heating
Lighting
Actuators
Controls
Plug Loads
[6 empty] | Sub-meters on equipment | [7 empty] | Permanent Sub-Metering | [6 empty] | Temporary Sub-Metering | [5 empty] | Busess Ducts
Permanent
Temporary
Single Phase Calculation
Three Phase Calculation
Name plate data
BOTTOM UP:
Motor Nameplate
Air Compressor Nameplate
Chiller Nameplate
RLA - "Running Load Amps" - current drawn during normal operation of electric motor, typically measured in plant operations
FLA - "Full Load Amps" - amount of current drawn when full-load torque and horsepower is reached for the motor, typically determined in a lab environment
The difference is in the fact that for FLA, you are looking at the rating of the MOTOR itself.
For RLA you are looking at how the motor runs relative to a particular load, e.g. a pump, or a fan, etc.
LRA - "Locked Rotor Amps" - current draw when the rotor is locked and not rotating, typically very high and not used for operational calculations
Typical EXAMPLE for Electrical
[13 empty] | Outside |  |  | Inside |  |  | 34% |  | To Motors Control Centers and Busess Ducts
3%
Busess Duct
100%
|  |  | Utility Substation Transformers | [16 empty] | 480 volt Distribution Center |  |  | 5% | [5 empty] | Local Disconnect
100 kV to 12, 470 volts
Three Phase
[5 empty] | kV = kilovolts | [10 empty] | In Plant Step-Down Transformer
12,470 volts to 480 volts
[18 empty] | Three Phase | [7 empty] | Motor Control Center |  |  | 50 hp Motor
[10 empty] | 60,000,000 kWh/year | [15 empty] | 3,000,000 kWh/year |  |  | Electrical End Use
[10 empty] | Total Electricity IN | [8 empty] | 20,400,000 kWh/year
[19 empty] | Distribution Center |  |  |  |  | 1,800,000 kWh/year |  |  |  | 238085.1064 |  | kWh/year
[24 empty] | Busess Duct |  |  |  | 0.3968%
|  | Liquid Propane: | [6 empty] | Gallons | [18 empty] | Based on:
|  |  | Delivery Tickets | [25 empty] | 6,000 hours per year
|  |  | Monthly Invoices | [25 empty] | 0.94 motor efficiency
|  |  | Submeters on processes | [25 empty] | 1.0 load factor
Is some of this pass through?
i.e. used to fuel trucks or buses
|  | Diesel Fuel: | [6 empty] | Gallons
Delivery Tickets
Monthly Invoices
Submeters on processes
Is some of this pass through?
i.e. used to fuel trucks or buses
Others
How delivered?
Units of delivery
Monthly invoices
M
M
M
M
M

## 3B_Process Block Diagrams
3B
SAMPLE ENERGY FLOW BLOCK DIAGRAMS
Reference Info
| Manufacturing Plant Example: Chiller Production | [10 empty] | Manufacturing Plant Example: Facility Equipment | [19 empty] | Manufacturing Plant Example: Facility Equipment
| Process Block Diagram with Energy | [10 empty] | Chiller System Details, Block Diagram | [19 empty] | Boilers and Hot Water System Details, Block Diagram
|  |  | KEY | IN and OUT | Process Step | Energy Loads |  | Energy Source |  | Waste Stream | Facility System |  |  | KEY | Energy Loads |  |  | Energy Source |  |  | Waste Stream |  |  | Facility System |  | Ambient Air |  |  | Hot Water Supply |  |  | KEY |  | Energy Loads |  | Energy Source |  | Process Step |  | Waste Stream |  | Facility System |  | Hot Water Supply |  | Hot Water Return
[5 empty] | City Water |  | Hot Water-Process |  | Test Water |  |  |  | Chilled Water Supply |  |  |  | Chilled Water Return |  |  | Tower Water SUP |  |  |  | Tower Water RET |  |  | City Water |  |  | Hot Water Return |  |  |  |  | Ambient Air |  | Combustion Air |  | Feed Water |  | Steam |  | Condensate Return |  | City Water
Warm Water to Tower
Cool Water from Tower
Hot Liquid
Exp Valve
Hot Vapor
Warm Vapor
[14 empty] | Cold Liquid | [6 empty] | Chilled Water Return
Chilled Water Supply
HW Return
[19 empty] | Hot Water Control Valve | [5 empty] | Chilled Water Control Valve
Return Air
Supply Air
Outside/Relief Air Dampers
Raw Materials-Water Cooled:
Steel Plate & Bar, Copper Tubes, Motors, Castings and Various Other Components
Final Products:
Water Cooled and Air Cooled Chiller Systems
Paint Booth
(air dried)
Packaging
Warehouse and Shipping
Steel Plate
Plasma Cutting
Motors
Electricity
Raw Materials-Air Cooled:
Heat Exchangers, Fans, Compressors, Motors, Enclosures and Various Other Components
Exhaust Fans
Steel Plate
Roll Forming
Vessel Welding
Water Cooled Chiller Test Lab
Copper Tubing Insertion
Compressed Gas & Hydrostatic Pressure Testing
Final Vessel Assembly
Compressor Assembly
Marriage Mount
Paint
Preparation
Compressor Component Machining
Plasma Cutters
Welder Power Supplies
Hydro Pumps
Air Cooled Unit Test Area
Exhaust Fans
Air Cooled Unit Assembly Lines
Hot Water Heaters to Load Air Cooled Chillers
Natural Gas
Test Water to Load Chillers
Chiller Compressor Motors
Compressor and Fan Motors
Used Hydro Water
Used Test Water
Test Pumps
Dirty Paint
Prep Water
Test Lab Water Control System
Electricity
Motors
Electricity
Gas Compressors
Electricity
Electricity
Electricity
Water Cooled Chillers/Cooling Towers
Water Cooled Chillers
Electricity
Compressors
Evaporators
Make Up Water
Electricity
Tower Fans
Condenser Water Pumps
Condensers
Cooling Towers
Electricity
Typical Air Handling Units (AHUs)
Chilled Water Loads:
Air Handling Unit Coils
Test Lab Water Control System
Pre-Filters
Return Air Fans
Electricity
Supply Air Fans
Electricity
Chilled Water Cooling Coil
Chilled Water
Pumps
Electricity
Hot Water Heating Coil
v
v
Flue Gas
Blow Down
Feed Water Pumps
BOILERS:
Building Heating
Process Heating
Test Lab Chiller Loading
Natural Gas
City Water - Makeup
Boilers and Hot Water
v
Electricity
Combustion Air Supply Fan Motors
Combustion Burners
Steam Hot Water Heaters
Feed Water Tank
Deaerating Feed Tank
DFT Pumps
Electricity
Hot Water Distribution Pumps
v
Electricity
Electricity
Hot Water Loads:
Air Handling Unit Coils
Process Hot Water
Test Lab Water Control System

## 3C_Elec Equip Master
3C |  |  | ANY SITE | [5 empty] | COLUMN COLOR KEY | [11 empty] | COLUMN COLOR KEY | [6 empty] | I = Intermittent, on and off, as needed, but not a continuous load, when ON, runs at full load | [22 empty] | COLUMN COLOR KEY |  |  |  |  | Pull Down Menu DATA | Sites ("D") | Electrical Phases ("T") | Load Type | Seasonal Load
|  |  |  | Electrical Equipment Master |  |  |  |  | DATA YOU CAN GET |  | NEW for 2022 | [9 empty] | DATA YOU CAN GET |  |  |  |  | Percent Factor |  | L = ON and runs continuously at FULL load during operations of associated manufacturing line | [12 empty] | 0.746 | kW/HP conversion factor | [8 empty] | DATA YOU CAN GET | [6 empty] | 1 | B | YES
[7 empty] | ALL electrical on ONE |  | DECISION NEEDED, then INPUT Values | [11 empty] | DECISION NEEDED, then INPUT Values |  |  |  | Winter Hours | 40% |  | V = Variable loads, equipment is ON, but ramps up and down depending on plant needs (air compressors, chillers, motors with VFDs) | [12 empty] | 90% | Power Factor | [8 empty] | DECISION NEEDED, then INPUT Values | [6 empty] | 3 | I | NO
[9 empty] | CALCULATED with FORMULA | [11 empty] | CALCULATED with FORMULA |  |  |  | Summer Hours | 60% |  | B = ON all the time (i.e. base load, servers, lighting, offices, fans, agitators etc.) | [11 empty] | Rarely Used | 100% | Derating for connected amp rating | [8 empty] | CALCULATED with FORMULA | [7 empty] | L
[7 empty] | Total Estimated ANNUAL kWh from this table: | 62094611.0511 | kWh | [18 empty] | DF = Diversity Factor, to account for things like oven heating, hot water heating heat trace tape, etc. (electric resistance heating) | [18 empty] | Must enter value or equation here if Column "T" = 1 | [11 empty] | V
[7 empty] | Total actual ANNUAL kWh from Duke Energy invoices: | 52686646.88 | kWh | [6 empty] | Must enter a ZERO for HP if a non-motor load | [8 empty] | Full Year | Plant Hours | OF | [13 empty] | BTUs/kWh | BTUs/kWh |  |  |  |  | For NON-Motor Loads
[5 empty] | For the year: |  | 2022 | [10 empty] | If HP = ZERO, then need these three | [5 empty] | PLANT Operational Factor: | 8760 | 7200 | 82.19% | OF = Operational Factor is for the plant. What percentage of the total time is the plant operating. | [12 empty] | 3412.14 | 3412.14 | 57.08% |  |  |  | Equation is |  |  |  |  | February | August
[7 empty] | DELTA: | 9407964.1711 | 17.86% | [8 empty] | NEED |  | NEED | NEED | [6 empty] | SF = Seasonal Factor should be YES for loads impacted by the season and weather conditions such as HVAC, boilers, and chillers, etc. | [12 empty] | CONVERT | [5 empty] | SITUATIONAL |  |  |  |  | Winter | Summer | Winter | Summer
For Sort | [5 empty] | SORT 1 | SORT 2 |  |  |  | SORT 3 | SORT 4 |  |  |  | Nameplate Data from Equipment or Info from Electrical One Line Diagram (record all available) | [11 empty] | OPS | SF | TOTAL HRS |  | PLANT | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer |  |  | Supplemental Electrical Information |  |  | Sub-Metering Info: Measured |  |  |  | Measured | Measured | Calculated | Calculated
#1 | #2 | #3 | SITE | BUILDING | DEPT. | GROUP | SYSTEM | AREA | LOCATION | EQUIPMENT | EQUIPMENT 1 | EQUIPMENT 2 | ASSET # | DESCRIPTION | QTY | HP | MEFF | RLA | FLA | PHASES | VOLTAGE | P. AMPS | SUB # | DIST # | MCC # | BUSS DUCT # | PANEL # | CODE | YES or NO | FULL YEAR | DF | OF | LF | LF | ∑HRS | ∑HRS | kW | kW | kWh | kWh | MMBTU | MMBTU | Any Additional Comments/Notes | HVAC/Chiller (TONS/Unit) | Lamps/Fixture | Watts/Lamp | Base kW | Metered | Recorded By | Verification | Calibration | kWh | kWh | kWh | kWh
1 | [5 empty] | PRODUCTION | PAINT | Chassis Wash Booth | Wash Booth (Line A) | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
2 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Wash Booth (Line A) | Exhaust Fan | MOTOR | FAN |  | Emission Point BO-EF1 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
3 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Wash Booth (Line A) | Exhaust Fan | MOTOR | FAN |  | Emission Point BO-EF2 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
4 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line A) | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
5 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line A) | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
6 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line A) | Exhaust Fan #1 | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
7 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line A) | Exhaust Fan # 2 | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
8 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
9 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #1 | Combustion Blower #1 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
10 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
11 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #1 | Combustion Blower # 2 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
12 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
13 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #1 | Combustion Blower # 3 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
14 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
15 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #1 | Combustion Blower # 4 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
16 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan #1 | MOTOR | FAN |  | Emission Point EP1-1 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
17 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan # 2 | MOTOR | FAN |  | Emission Point EP1-2 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
18 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan # 3 | MOTOR | FAN |  | Emission Point EP1-3 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
19 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan # 4 | MOTOR | FAN |  | Emission Point EP1-4 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
20 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan # 5 | MOTOR | FAN |  | Emission Point EP1-5 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
21 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan # 6 | MOTOR | FAN |  | Emission Point EP1-6 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
22 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan # 7 | MOTOR | FAN |  | Emission Point EP1-7 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
23 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan # 8 | MOTOR | FAN |  | Emission Point EP1-8 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
24 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan # 9 | MOTOR | FAN |  | Emission Point EP1-9 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
25 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line A) Exhaust | Exhaust Fan #10 | MOTOR | FAN |  | Emission Point EP1-10 | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
26 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Heater Box (Line A) | Combustion Blower #1 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
27 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line A) | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
28 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line A) | Recirculating Fan # 2 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 3.2137 | 3.2137 | 9255.3705 | 13883.0557 | 31.5806 | 47.3709 | [11 empty] | 9255.3705 | 13883.0557
29 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Heater Box (Line A) | Combustion Blower # 2 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
30 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line A) | Recirculating Fan # 3 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
31 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line A) | Recirculating Fan # 4 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
32 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Heater Box (Line A) | Combustion Blower # 3 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
33 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line A) | Recirculating Fan # 5 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
34 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line A) | Recirculating Fan # 6 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
35 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Oven (Line A) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
36 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Cooling Tunnel (Line A) | Supply Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
37 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Cooling Tunnel (Line A) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
38 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Cooling Tunnel (Line A) | Recirculating Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
39 | [5 empty] | PRODUCTION | PAINT | Chassis Wash Booth | Wash Booth (Line B) | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
40 | [5 empty] | PRODUCTION | PAINT | Chassis Wash Booth | Wash Booth (Line B) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
41 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line B) | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
42 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line B) | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
43 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line B) | Exhaust Fan #1 | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
44 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line B) | Exhaust Fan # 2 | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
45 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | ASH # 2 | Supply Fan | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 29.4151 | 29.4151 | 84715.5312 | 127073.2968 | 289.0613 | 433.5919 | [11 empty] | 84715.5312 | 127073.2968
46 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH # 2 | Combustion Blower #1 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
47 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | ASH # 2 | Supply Fan | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 29.4151 | 29.4151 | 84715.5312 | 127073.2968 | 289.0613 | 433.5919 | [11 empty] | 84715.5312 | 127073.2968
48 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH # 2 | Combustion Blower # 2 | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
49 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line B) Exhaust | Exhaust Fan #1 | MOTOR | FAN |  | Emission Point EP2-1 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
50 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line B) Exhaust | Exhaust Fan # 2 | MOTOR | FAN |  | Emission Point EP2-2 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
51 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line B) Exhaust | Exhaust Fan # 3 | MOTOR | FAN |  | Emission Point EP2-3 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
52 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line B) Exhaust | Exhaust Fan # 4 | MOTOR | FAN |  | Emission Point EP2-4 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
53 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line B) Exhaust | Exhaust Fan # 5 | MOTOR | FAN |  | Emission Point EP2-5 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
54 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line B) Exhaust | Exhaust Fan # 6 | MOTOR | FAN |  | Emission Point EP2-6 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
55 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line B) Exhaust | Exhaust Fan # 7 | MOTOR | FAN |  | Emission Point EP2-7 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
56 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Paint Booth (Line B) Exhaust | Exhaust Fan # 8 | MOTOR | FAN |  | Emission Point EP2-8 | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
57 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line B) | Supply Fan | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 29.4151 | 29.4151 | 84715.5312 | 127073.2968 | 289.0613 | 433.5919 | [11 empty] | 84715.5312 | 127073.2968
58 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Heater Box (Line B) | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
59 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Oven (Line B) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
60 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line B) | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
61 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line B) | Recirculating Fan # 2 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
62 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line B) | Recirculating Fan # 3 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
63 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line B) | Recirculating Fan # 4 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
64 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line B) | Recirculating Fan # 5 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
65 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Oven (Line B) | Recirculating Fan # 6 | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
66 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Cooling Tunnel (Line B) | Supply Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
67 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Cooling Tunnel (Line B) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
68 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Cooling Tunnel (Line B) | Recirculating Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
69 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 1 | Booth No. 1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP29-1 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
70 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 1 | Booth No. 1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP29-2 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
71 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 1 | Booth No. 1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP29-3 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
72 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 1 | Booth No. 1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP29-4 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
73 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 1 | Booth No. 1 | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 50 | 89.25% | 62 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 31.3445 | 31.3445 | 90272.2689 | 135408.4034 | 308.0216 | 462.0324 | [11 empty] | 90272.2689 | 135408.4034
74 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 2 | Booth No. 2 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP30-1 | 1 | 7.5 | 87.05% | 9.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
75 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 2 | Booth No. 2 | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 25 | 90.05% | 34 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 15.533 | 15.533 | 44735.1471 | 67102.7207 | 152.6426 | 228.9639 | [11 empty] | 44735.1471 | 67102.7207
76 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 3 | Booth No. 3 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP31-1 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
77 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 3 | Booth No. 3 | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 9.5532 | 9.5532 | 27513.2612 | 41269.8919 | 93.8791 | 140.8186 | [11 empty] | 27513.2612 | 41269.8919
78 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 4 | Booth No. 4 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP32-1 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
79 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 4 | Booth No. 4 | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 20 | 89.7% | 24.7 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 12.4749 | 12.4749 | 35927.7592 | 53891.6388 | 122.5905 | 183.8858 | [11 empty] | 35927.7592 | 53891.6388
80 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 5 | Booth No. 5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP33-1 | 1 | 7.5 | 87.05% | 9.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
81 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 5 | Booth No. 5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP33-2 | 1 | 7.5 | 87.05% | 9.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
82 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 5 | Booth No. 5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP33-3 | 1 | 7.5 | 87.05% | 9.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
83 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 5 | Booth No. 5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP33-4 | 1 | 7.5 | 87.05% | 9.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
84 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 5 | Booth No. 5 | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 25.0756 | 25.0756 | 72217.8151 | 108326.7227 | 246.4173 | 369.6259 | [11 empty] | 72217.8151 | 108326.7227
85 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 6 | Booth No. 6 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP34-1 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
86 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 6 | Booth No. 6 | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 25.0756 | 25.0756 | 72217.8151 | 108326.7227 | 246.4173 | 369.6259 | [11 empty] | 72217.8151 | 108326.7227
87 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 7 | Booth No. 7 Small Parts | Exhaust Fan | MOTOR | FAN |  | Emission Point EP44-1 | 1 | 7.5 | 87.05% | 9.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
88 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 7 | Booth No. 7 Small Parts | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 6.4273 | 6.4273 | 18510.741 | 27766.1114 | 63.1612 | 94.7419 | [11 empty] | 18510.741 | 27766.1114
89 | [5 empty] | PRODUCTION | PAINT | Sanding Area No. 5 | Color No. 5 - In Sanding Area | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
90 | [5 empty] | PRODUCTION | PAINT | Sanding Area No. 5 | Color No. 5 - In Sanding Area | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
91 | [5 empty] | PRODUCTION | PAINT | Sanding Area No. 5 | Color No. 5 - In Sanding Area | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
92 | [5 empty] | PRODUCTION | PAINT | Sanding Area No. 5 | Color No. 5 - In Sanding Area | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
93 | [5 empty] | PRODUCTION | PAINT | Sanding Area No. 6 | Color No. 6 - In Sanding Area | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
94 | [5 empty] | PRODUCTION | PAINT | Sanding Area No. 6 | Color No. 6 - In Sanding Area | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
95 | [5 empty] | PRODUCTION | PAINT | Sanding Area No. 6 | Color No. 6 - In Sanding Area | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
96 | [5 empty] | PRODUCTION | PAINT | Sanding Area No. 6 | Color No. 6 - In Sanding Area | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
97 | [5 empty] | PRODUCTION | PAINT | Hood Prep Booth | Air Supply House | Recirculation Fan | MOTOR | FAN |  |  | 1 | 30 | 90.85% | 40 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 14.7804 | 14.7804 | 42567.5729 | 63851.3594 | 145.2465 | 217.8698 | [11 empty] | 42567.5729 | 63851.3594
98 | [5 empty] | PRODUCTION | PAINT | Hood Sludge System | Sludge Pump No. 1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
99 | [5 empty] | PRODUCTION | PAINT | Hood Sludge System | Sludge Pump No. 2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
100 | [5 empty] | PRODUCTION | PAINT | Hood Sludge System | Sludge Pump No. 3 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
101 | [5 empty] | PRODUCTION | PAINT | Hood Sludge System | Sludge Consolidation Pump | Pump Motor | MOTOR | PUMP |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
102 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Circulation Pump Stage #1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
103 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Circulation Pump Stage #2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
104 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Circulation Pump Stage #3 | Pump Motor | MOTOR | PUMP |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
105 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Blow-Off Circulation Fan #1 | Blower Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 6.4273 | 6.4273 | 18510.741 | 27766.1114 | 63.1612 | 94.7419 | [11 empty] | 18510.741 | 27766.1114
106 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Blow-Off Circulation Fan #2 | Blower Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 6.4273 | 6.4273 | 18510.741 | 27766.1114 | 63.1612 | 94.7419 | [11 empty] | 18510.741 | 27766.1114
107 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Hood Washer | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
108 | [5 empty] | PRODUCTION | PAINT | Hood Dry-Off Oven | Dry-Off Oven (D122LOS) | Recirculation Fan | MOTOR | FAN |  |  | 1 | 50 | 89.25% | 65 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 25.0756 | 25.0756 | 72217.8151 | 108326.7227 | 246.4173 | 369.6259 | [11 empty] | 72217.8151 | 108326.7227
109 | [5 empty] | PRODUCTION | PAINT | Hood Dry-Off Oven | Dry-Off Oven (D126LOS) | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
110 | [5 empty] | PRODUCTION | PAINT | Hood Dry-Off Oven | Dry Off Oven Exhaust | Exhaust Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
111 | [5 empty] | PRODUCTION | PAINT | Hood Dry-Off Oven | Cooling Tunnel (D134LOS) | Recirculation Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
112 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Hot Water Circulation Pump #1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
113 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Hot Water Circulation Pump #2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
114 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Chilled Water Circulation Pump #1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
115 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Chilled Water Circulation Pump #2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
116 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Hot Water Boiler | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
117 | [5 empty] | PRODUCTION | PAINT | Hood Paint Spray Booth | Tack-Off Booth (D206LOS) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
118 | [5 empty] | PRODUCTION | PAINT | Hood Paint Spray Booth | Prep Booth Manual Cut-In (D202LOS) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 77 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 29.4151 | 29.4151 | 84715.5312 | 127073.2968 | 289.0613 | 433.5919 | [11 empty] | 84715.5312 | 127073.2968
119 | [5 empty] | PRODUCTION | PAINT | Hood Paint Spray Booth | Base Coat ASH | Supply Fan | MOTOR | FAN |  |  | 1 | 150 | 92.8% | 180 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 90.4364 | 90.4364 | 260456.8966 | 390685.3448 | 888.7154 | 1333.0731 | [11 empty] | 260456.8966 | 390685.3448
120 | [5 empty] | PRODUCTION | PAINT | Hood Paint Spray Booth | Base Coat Flash-Off (D214LOS) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
121 | [5 empty] | PRODUCTION | PAINT | Hood Clear Coat Booth | Clear Coat Air House | Supply Fan | MOTOR | FAN |  |  | 1 | 150 | 92.8% | 180 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 90.4364 | 90.4364 | 260456.8966 | 390685.3448 | 888.7154 | 1333.0731 | [11 empty] | 260456.8966 | 390685.3448
122 | [5 empty] | PRODUCTION | PAINT | Hood Clear Coat Booth | Robot Automation Spray | Control Panel | PANEL | ROBOT |  | Control Panel for Robot | 1 | 0 |  | 16.7 |  | 3 | 480 | [6 empty] | I | NO | 8760 | 100% | 82.19% | 25% | 25% | 2880 | 4320 | 3.1238 | 3.1238 | 8996.6454 | 13494.9681 | 30.6978 | 46.0467 | [11 empty] | 8996.6454 | 13494.9681
123 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Hood Oven Heater Box Zone #1 | Recirculation Fan | MOTOR | FAN |  | Emission Point HP-E13 | 1 | 50 | 89.25% | 64 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 25.0756 | 25.0756 | 72217.8151 | 108326.7227 | 246.4173 | 369.6259 | [11 empty] | 72217.8151 | 108326.7227
124 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Hood Oven Heater Box Zone #1 | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
125 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Hood Oven Zone #1 | Exhaust Fan | MOTOR | FAN |  | Emission Point HP-E12 | 1 | 10 | 87.05% | 23 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
126 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Hood Oven Heater Box Zone #2 | Recirculation Fan | MOTOR | FAN |  | Emission Point HP-E11 | 1 | 50 | 89.25% | 64 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 25.0756 | 25.0756 | 72217.8151 | 108326.7227 | 246.4173 | 369.6259 | [11 empty] | 72217.8151 | 108326.7227
127 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Hood Oven Heater Box Zone #2 | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
128 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Hood Oven Zone #2 | Exhaust Fan | MOTOR | FAN |  | Emission Point HP-E12 | 1 | 10 | 87.05% | 23 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
129 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Recirculation Cooling Tunnel | Recirculation Fan | MOTOR | FAN |  | Emission Point HP-E10 | 1 | 50 | 89.25% | 64 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 25.0756 | 25.0756 | 72217.8151 | 108326.7227 | 246.4173 | 369.6259 | [11 empty] | 72217.8151 | 108326.7227
130 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Air Supply House #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
131 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Burner | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
132 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #2 | Booth #1 Air Supply House #2 | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
133 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #2 | Booth #2 Burner | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
134 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Exhaust Fan #1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP38-1 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
135 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Exhaust Fan #2 | Exhaust Fan | MOTOR | COMB BLOWER |  | Emission Point EP38-2 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
136 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Exhaust Fan #3 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP38-3 | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
137 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Exhaust Fan #4 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP38-4 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
138 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Exhaust Fan #5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP38-5 | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
139 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Oven Heater Box | Supply Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
140 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Oven Heater Box | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 1 | 87.05% | 2.1 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.64273 | 0.64273 | 1851.0741 | 2776.6111 | 6.3161 | 9.4742 | [11 empty] | 1851.0741 | 2776.6111
141 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Oven Fans | Recirculation Fan | MOTOR | FAN |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
142 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Oven Exhaust | Exhaust Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
143 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth Air House - North | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
144 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth North AHU Burner | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
145 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth Air House - South | Supply Fan | MOTOR | FAN |  |  | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
146 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth South AHU Burner | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
147 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth Exhaust Fan #1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP39-1 | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 7.6426 | 7.6426 | 22010.609 | 33015.9135 | 75.1033 | 112.6549 | [11 empty] | 22010.609 | 33015.9135
148 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth Exhaust Fan #2 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP39-2 | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
149 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth Exhaust Fan #3 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP39-3 | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
150 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth Exhaust Fan #4 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP39-4 | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 7.6426 | 7.6426 | 22010.609 | 33015.9135 | 75.1033 | 112.6549 | [11 empty] | 22010.609 | 33015.9135
151 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth Flash-Off | Exhaust Fan | MOTOR | FAN |  | Emission Point EP39-5 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
152 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Radian Zone | Combustion Blower | MOTOR | COMB BLOWER |  | Emission Point MTR 210 | 1 | 1 | 87.05% | 2.1 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.64273 | 0.64273 | 1851.0741 | 2776.6111 | 6.3161 | 9.4742 | [11 empty] | 1851.0741 | 2776.6111
153 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Radian Zone | Fresh Air Supply Fan | MOTOR | FAN |  | Emission Point MTR 206 | 1 | 1 | 87.05% | 2.1 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 0.51419 | 0.51419 | 1480.8593 | 2221.2889 | 5.0529 | 7.5793 | [11 empty] | 1480.8593 | 2221.2889
154 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Radian Zone | Turbulator Fan #1 | MOTOR | FAN |  | Emission Point MTR 350 | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
155 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Radian Zone | Turbulator Fan # 2 | MOTOR | FAN |  | Emission Point MTR 352 | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
156 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Radian Zone | Exhaust Fan | MOTOR | FAN |  | Emission Point MTR 208 | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
157 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Turbulent Zone | Combustion Blower | MOTOR | COMB BLOWER |  | Emission Point MTR 356 | 1 | 1 | 87.05% | 2.1 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.64273 | 0.64273 | 1851.0741 | 2776.6111 | 6.3161 | 9.4742 | [11 empty] | 1851.0741 | 2776.6111
158 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Turbulent Zone | Supply Fan | MOTOR | FAN |  | Emission Point MTR 354 | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
159 | [5 empty] | FACILITY | WWTP | Waste Treatment | Equalizer Tank #1 | Transfer Pump | MOTOR | PUMP |  |  | 1 | 2 | 87.05% | 1.5 |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
160 | [5 empty] | FACILITY | WWTP | Waste Treatment | Equalizer Tank #2 | Transfer Pump | MOTOR | PUMP |  |  | 1 | 2 | 87.05% | 1.5 |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
161 | [5 empty] | FACILITY | WWTP | Waste Treatment | Neutralizer Tank Transfer Pump #1 | Transfer Pump | MOTOR | PUMP |  |  | 1 | 2 | 87.05% | 1.5 |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
162 | [5 empty] | FACILITY | WWTP | Waste Treatment | Neutralizer Tank Transfer Pump #2 | Transfer Pump | MOTOR | PUMP |  |  | 1 | 2 | 87.05% | 1.5 |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
163 | [5 empty] | FACILITY | WWTP | Waste Treatment | Reaction Tank #3 Agitator | Mix Tank Agitator | MOTOR | MIXER |  |  | 1 | 0.25 | 80% | 5.8 |  | 1 | 120 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
164 | [5 empty] | FACILITY | WWTP | Waste Treatment | Reaction Tank #4 Agitator | Mix Tank Agitator | MOTOR | MIXER |  |  | 1 | 0.25 | 80% | 5.8 |  | 1 | 120 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
165 | [5 empty] | FACILITY | WWTP | Waste Treatment | Neutralization Tank #5 Agitator | Mix Tank Agitator | MOTOR | MIXER |  |  | 1 | 0.25 | 80% | 5.8 |  | 1 | 120 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
166 | [5 empty] | FACILITY | WWTP | Waste Treatment | Neutralization Tank #6 Agitator | Mix Tank Agitator | MOTOR | MIXER |  |  | 1 | 0.25 | 80% | 5.8 |  | 1 | 120 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
167 | [5 empty] | FACILITY | WWTP | Waste Treatment | Lamella Clarifier Agitator #1 | Mix Tank Agitator | MOTOR | MIXER |  |  | 1 | 0.25 | 80% | 5.8 |  | 1 | 120 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
168 | [5 empty] | FACILITY | WWTP | Waste Treatment | Lamella Clarifier Agitator #2 | Mix Tank Agitator | MOTOR | MIXER |  |  | 1 | 0.25 | 80% | 5.8 |  | 1 | 120 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
169 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Clean Spray Stage No. 1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
170 | [5 empty] | PRODUCTION | PAINT | Pretreatment | City Water Rinse Stage No. 2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 25 | 90.05% | 34 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 12.4264 | 12.4264 | 35788.1177 | 53682.1766 | 122.1141 | 183.1711 | [11 empty] | 35788.1177 | 53682.1766
171 | [5 empty] | PRODUCTION | PAINT | Pretreatment | City Water Rinse Stage No. 3 | Pump Motor | MOTOR | PUMP |  |  | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 7.6426 | 7.6426 | 22010.609 | 33015.9135 | 75.1033 | 112.6549 | [11 empty] | 22010.609 | 33015.9135
172 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Zinc Phosphate Stage No. 4 | Pump Motor | MOTOR | PUMP |  |  | 1 | 40 | 89.25% | 52 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
173 | [5 empty] | PRODUCTION | PAINT | Pretreatment | City Water Rinse Stage No. 5 | Pump Motor | MOTOR | PUMP |  |  | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 7.6426 | 7.6426 | 22010.609 | 33015.9135 | 75.1033 | 112.6549 | [11 empty] | 22010.609 | 33015.9135
174 | [5 empty] | PRODUCTION | PAINT | Pretreatment | City Water Rinse Stage No. 6 | Pump Motor | MOTOR | PUMP |  |  | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 7.6426 | 7.6426 | 22010.609 | 33015.9135 | 75.1033 | 112.6549 | [11 empty] | 22010.609 | 33015.9135
175 | [5 empty] | PRODUCTION | PAINT | Pretreatment | DI Water Supply Pump | Pump Motor | MOTOR | PUMP |  |  | 1 | 5 | 87.05% | 7.6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 2.5709 | 2.5709 | 7404.2964 | 11106.4446 | 25.2645 | 37.8967 | [11 empty] | 7404.2964 | 11106.4446
176 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Entrance Air Seal | Exhaust Fan | MOTOR | FAN |  | Emission Point EP28-1 | 1 | 7.5 | 87.05% | 6 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
177 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Pretreat | Exhaust Fan | MOTOR | FAN |  | Emission Point EP28-2 | 1 | 1 | 87.05% | 4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 0.51419 | 0.51419 | 1480.8593 | 2221.2889 | 5.0529 | 7.5793 | [11 empty] | 1480.8593 | 2221.2889
178 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Pretreat | Exhaust Fan | MOTOR | FAN |  | Emission Point EP28-3 | 1 | 1 | 87.05% | 4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 0.51419 | 0.51419 | 1480.8593 | 2221.2889 | 5.0529 | 7.5793 | [11 empty] | 1480.8593 | 2221.2889
179 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Pretreat | Exhaust Fan | MOTOR | FAN |  | Emission Point EP28-4 | 1 | 1 | 87.05% | 4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 0.51419 | 0.51419 | 1480.8593 | 2221.2889 | 5.0529 | 7.5793 | [11 empty] | 1480.8593 | 2221.2889
180 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Exit Air Seal | Exhaust Fan | MOTOR | FAN |  | Emission Point EP28-5 | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
181 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Hot Water Recirculating Pump | Pump Motor | MOTOR | PUMP |  | Pump motor in Boiler Room (PNL D7.5A) | 1 | 40 | 89.25% | 52 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
182 | [5 empty] | PRODUCTION | PAINT | Pretreatment | Hot Water Boiler Heater | Combustion Blower | MOTOR | COMB BLOWER |  | Pump motor in Boiler Room (PNL D7.5A) | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
183 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven Heater Box | Supply Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
184 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven Heater Box | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 1.9282 | 1.9282 | 5553.2223 | 8329.8334 | 18.9484 | 28.4226 | [11 empty] | 5553.2223 | 8329.8334
185 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
186 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Recirculating Fan # 2 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
187 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Recirculating Fan # 3 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
188 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Recirculating Fan # 4 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
189 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Recirculating Fan # 5 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
190 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Recirculating Fan # 6 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
191 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Recirculating Fan # 7 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
192 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Recirculating Fan # 8 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
193 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven | Exhaust Fan | MOTOR | FAN |  | Emission Point EP58-1 | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
194 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven Cooling Tunnel | CT Recirculation Fan #1 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
195 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven Cooling Tunnel | CT Recirculation Fan #2 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
196 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven Cooling Tunnel | Supply Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
197 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven Cooling Tunnel | Exhaust Fan | MOTOR | FAN |  | Emission Point EP5-1 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
198 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Prep & Tack-Off | Exhaust Fan | MOTOR | FAN |  | Emission Point EP3-1 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
199 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Prep & Tack-Off | Exhaust Fan | MOTOR | FAN |  | Emission Point EP3-2 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
200 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Prep & Tack-Off | Exhaust Fan | MOTOR | FAN |  | Emission Point EP3-3 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
201 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Prep & Tack-Off | Exhaust Fan | MOTOR | FAN |  | Emission Point EP3-4 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
202 | [5 empty] | PRODUCTION | PAINT | Supply Primer Booth | ASH #5B | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% | 92 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 46.0368 | 46.0368 | 132585.8475 | 198878.7713 | 452.4015 | 678.6022 | [11 empty] | 132585.8475 | 198878.7713
203 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Paint Booth | Exhaust Fan | MOTOR | FAN |  | Emission Point EP4-1 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
204 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Paint Booth | Exhaust Fan | MOTOR | FAN |  | Emission Point EP4-2 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
205 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Paint Booth | Exhaust Fan | MOTOR | FAN |  | Emission Point EP4-3 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
206 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Paint Booth | Exhaust Fan | MOTOR | FAN |  | Emission Point EP4-4 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
207 | [5 empty] | PRODUCTION | PAINT | Primer Sludge System | Sludge Pump No. 1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
208 | [5 empty] | PRODUCTION | PAINT | Primer Sludge System | Sludge Pump No. 2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
209 | [5 empty] | PRODUCTION | PAINT | Primer Sludge System | Sludge Consolidator Pump | Pump Motor | MOTOR | PUMP |  |  | 1 | 2 | 87.05% | 3.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
210 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Primer Flash-Off Exhaust Fan | Exhaust Fan | MOTOR | FAN |  | Emission Point EP4A-1 | 1 | 3 | 87.05% | 4.5 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
211 | [5 empty] | PRODUCTION | PAINT | Primer Spray Booth | Robot Automation Prime Booth | Control Panel | PANEL | ROBOT |  | Control Panel for Robot | 1 | 0 |  | 16.7 |  | 3 | 480 | [6 empty] | I | NO | 8760 | 100% | 82.19% | 25% | 25% | 2880 | 4320 | 3.1238 | 3.1238 | 8996.6454 | 13494.9681 | 30.6978 | 46.0467 | [11 empty] | 8996.6454 | 13494.9681
212 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Heater Box | Supply Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
213 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Heater Box (Combustion) | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 0.75 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.48205 | 0.48205 | 1388.3056 | 2082.4584 | 4.7371 | 7.1056 | [11 empty] | 1388.3056 | 2082.4584
214 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Entrance Air Seal | Air Seal Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
215 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Primer Oven Exhaust | Exhaust Fan | MOTOR | FAN |  |  | 1 | 2 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
216 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Exit Air Seal | Air Seal Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
217 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Entrance End | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
218 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Entrance End | Recirculating Fan #2 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
219 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Entrance End | Recirculating Fan #3 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
220 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Exit End | Recirculating Fan #4 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
221 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Exit End | Recirculating Fan #5 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
222 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Exit End | Recirculating Fan #6 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
223 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Primer Oven Cooling Tunnel | Exhaust Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
224 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Primer Oven Cooling Tunnel | Supply Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
225 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Primer Oven Cooling Tunnel | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
226 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Primer Oven Cooling Tunnel | Recirculating Fan #2 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
227 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | ASH #5A | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 36.8294 | 36.8294 | 106068.678 | 159103.017 | 361.9212 | 542.8818 | [11 empty] | 106068.678 | 159103.017
228 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth Plenum | Recirculation Fan # - 1 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
229 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth Plenum | Recirculation Fan # - 2 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
230 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth Plenum | Recirculation Fan # - 3 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
231 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth Plenum | Recirculation Fan # - 4 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
232 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth Plenum | Recirculation Fan # - 5 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
233 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth Plenum | Recirculation Fan # - 6 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
234 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth Plenum | Recirculation Fan # - 7 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
235 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth Plenum | Recirculation Fan # - 8 | MOTOR | FAN |  |  | 1 | 3 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
236 | [5 empty] | PRODUCTION | PAINT | Primer Sand Booth | Primer Sand Booth | Exhaust Fan | MOTOR | FAN |  | Emission Point EP58-2 | 1 | 7.5 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
237 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 46.0368 | 46.0368 | 132585.8475 | 198878.7713 | 452.4015 | 678.6022 | [11 empty] | 132585.8475 | 198878.7713
238 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 46.0368 | 46.0368 | 132585.8475 | 198878.7713 | 452.4015 | 678.6022 | [11 empty] | 132585.8475 | 198878.7713
239 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Tack Booth No. 1 | Exhaust Fan #1 | MOTOR | FAN |  | Emission Point EP47-1 | 1 | 7.5 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
240 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Tack Booth No. 1 | Exhaust Fan #2 | MOTOR | FAN |  | Emission Point EP47-2 | 1 | 7.5 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
241 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 1 | Booth No. 1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP7-1 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
242 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 1 | Booth No. 1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP7-2 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
243 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 1 | Booth No. 1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP7-3 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
244 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 1 | Booth No. 1 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP7-4 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
245 | [5 empty] | PRODUCTION | PAINT | Paint Spray No. 2 | Robot Automation Booth No. 1 | Control Panel | PANEL | ROBOT |  | Control Panel for Robot | 1 | 0 |  | 16.7 |  | 3 | 480 | [6 empty] | I | NO | 8760 | 100% | 82.19% | 25% | 25% | 2880 | 4320 | 3.1238 | 3.1238 | 8996.6454 | 13494.9681 | 30.6978 | 46.0467 | [11 empty] | 8996.6454 | 13494.9681
246 | [5 empty] | PRODUCTION | PAINT | Color No. 1 Sludge | Sludge Pump No. 1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
247 | [5 empty] | PRODUCTION | PAINT | Color No. 1 Sludge | Sludge Pump No. 2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
248 | [5 empty] | PRODUCTION | PAINT | Color No. 1 Sludge | Sludge Consolidator Pump PALIN | Pump Motor | MOTOR | PUMP |  |  | 1 | 2 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
249 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Tack-Off | ASH #3 | Supply Fan | MOTOR | FAN |  |  | 1 | 60 | 91.3% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 36.7689 | 36.7689 | 105894.414 | 158841.621 | 361.3266 | 541.9898 | [11 empty] | 105894.414 | 158841.621
250 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Tack Booth No. 2 | Exhaust Fan #1 | MOTOR | FAN |  | Emission Point EP48-1 | 1 | 7.5 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
251 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Tack Booth No. 2 | Exhaust Fan #2 | MOTOR | FAN |  | Emission Point EP48-2 | 1 | 7.5 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 4.8205 | 4.8205 | 13883.0557 | 20824.5836 | 47.3709 | 71.0564 | [11 empty] | 13883.0557 | 20824.5836
252 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 46.0368 | 46.0368 | 132585.8475 | 198878.7713 | 452.4015 | 678.6022 | [11 empty] | 132585.8475 | 198878.7713
253 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Booth No. 2 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP8-1 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
254 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Booth No. 2 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP8-2 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
255 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Booth No. 2 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP8-3 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
256 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Booth No. 2 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP8-4 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
257 | [5 empty] | PRODUCTION | PAINT | Paint Spray No. 2 | Robot Automation Booth No. 2 | Control Panel | PANEL | ROBOT |  | Control Panel for Robot | 1 | 0 |  | 16.7 |  | 3 | 480 | [6 empty] | I | NO | 8760 | 100% | 82.19% | 25% | 25% | 2880 | 4320 | 3.1238 | 3.1238 | 8996.6454 | 13494.9681 | 30.6978 | 46.0467 | [11 empty] | 8996.6454 | 13494.9681
258 | [5 empty] | PRODUCTION | PAINT | Color No. 2 Sludge | Sludge Pump No. 1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
259 | [5 empty] | PRODUCTION | PAINT | Color No. 2 Sludge | Sludge Pump No. 2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
260 | [5 empty] | PRODUCTION | PAINT | Color No. 2 Sludge | Sludge Consolidator Pump PALIN | Pump Motor | MOTOR | PUMP |  |  | 1 | 2 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
261 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Tunnel Fan #1 | Exhaust Fan #1 | MOTOR | FAN |  |  | 1 | 10 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
262 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 2 | Tunnel Fan #2 | Exhaust Fan #2 | MOTOR | FAN |  |  | 1 | 10 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
263 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Tack-Off | ASH #3 | Supply Fan | MOTOR | FAN |  |  | 1 | 60 | 91.3% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 36.7689 | 36.7689 | 105894.414 | 158841.621 | 361.3266 | 541.9898 | [11 empty] | 105894.414 | 158841.621
264 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 3 | Tack Booth No. 3 | Exhaust Fan #1 | MOTOR | FAN |  | Emission Point EP49-1 | 1 | 10 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
265 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 3 | Tack Booth No. 3 | Exhaust Fan #2 | MOTOR | FAN |  | Emission Point EP49-2 | 1 | 10 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
266 | [5 empty] | PRODUCTION | PAINT | Booth #3 Cut-In | ASH #9 | Supply Fan #1 | MOTOR | FAN |  |  | 1 | 100 | 91.65% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 61.0475 | 61.0475 | 175816.6939 | 263725.0409 | 599.9112 | 899.8668 | [11 empty] | 175816.6939 | 263725.0409
267 | [5 empty] | PRODUCTION | PAINT | Booth #3 Cut-In | ASH #9 | Supply Fan # 2 | MOTOR | FAN |  |  | 1 | 100 | 91.65% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 61.0475 | 61.0475 | 175816.6939 | 263725.0409 | 599.9112 | 899.8668 | [11 empty] | 175816.6939 | 263725.0409
268 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 3 | Cut-In Fan #1 | Exhaust Fan #1 | MOTOR | FAN |  | Emission Point EP49-3 | 1 | 10 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
269 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 3 | Cut-In Fan #2 | Exhaust Fan #2 | MOTOR | FAN |  | Emission Point EP49-4 | 1 | 10 | 87.05% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
270 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 46.0368 | 46.0368 | 132585.8475 | 198878.7713 | 452.4015 | 678.6022 | [11 empty] | 132585.8475 | 198878.7713
271 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 46.0368 | 46.0368 | 132585.8475 | 198878.7713 | 452.4015 | 678.6022 | [11 empty] | 132585.8475 | 198878.7713
272 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 3 | Booth No. 3 Base Coat | Exhaust Fan | MOTOR | FAN |  | Emission Point EP9-1 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
273 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 3 | Booth No. 3 Base Coat | Exhaust Fan | MOTOR | FAN |  | Emission Point EP9-2 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
274 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 3 | Booth No. 3 Clear Coat | Exhaust Fan | MOTOR | FAN |  | Emission Point EP9-3 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
275 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 3 | Booth No. 3 Clear Coat | Exhaust Fan | MOTOR | FAN |  | Emission Point EP9-4 | 1 | 40 | 89.25% |  |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
276 | [5 empty] | PRODUCTION | PAINT | Paint Spray No. 2 | Robot Automation Booth No. 3 | Control Panel | PANEL | ROBOT |  | Control Panel for Robot | 1 | 0 |  | 16.7 |  | 3 | 480 | [6 empty] | I | NO | 8760 | 100% | 82.19% | 25% | 25% | 2880 | 4320 | 3.1238 | 3.1238 | 8996.6454 | 13494.9681 | 30.6978 | 46.0467 | [11 empty] | 8996.6454 | 13494.9681
277 | [5 empty] | PRODUCTION | PAINT | Paint Spray No. 2 | Robot Automation Booth No. 3 | Control Panel | PANEL | ROBOT |  | Control Panel for Robot | 1 | 0 |  | 16.7 |  | 3 | 480 | [6 empty] | I | NO | 8760 | 100% | 82.19% | 25% | 25% | 2880 | 4320 | 3.1238 | 3.1238 | 8996.6454 | 13494.9681 | 30.6978 | 46.0467 | [11 empty] | 8996.6454 | 13494.9681
278 | [5 empty] | PRODUCTION | PAINT | Color No. 3 Sludge | Sludge Pump No. 1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
279 | [5 empty] | PRODUCTION | PAINT | Color No. 3 Sludge | Sludge Pump No. 2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
280 | [5 empty] | PRODUCTION | PAINT | Color No. 3 Sludge | Sludge Consolidator Pump PALIN | Pump Motor | MOTOR | PUMP |  |  | 1 | 2 | 87.05% | 3.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
281 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 4 | Booth No. 4 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP10-1 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
282 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 4 | Booth No. 4 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP10-2 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
283 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 4 | Booth No. 4 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP10-3 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
284 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 4 | Booth No. 4 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP10-4 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
285 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Supply Fan #1 | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 36.7689 | 36.7689 | 105894.414 | 158841.621 | 361.3266 | 541.9898 | [11 empty] | 105894.414 | 158841.621
286 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Supply Fan # 2 | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 36.7689 | 36.7689 | 105894.414 | 158841.621 | 361.3266 | 541.9898 | [11 empty] | 105894.414 | 158841.621
287 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Supply Fan # 3 | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 36.7689 | 36.7689 | 105894.414 | 158841.621 | 361.3266 | 541.9898 | [11 empty] | 105894.414 | 158841.621
288 | [5 empty] | PRODUCTION | PAINT | Color No. 4 Sludge | Sludge Pump No. 1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
289 | [5 empty] | PRODUCTION | PAINT | Color No. 4 Sludge | Sludge Pump No. 2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
290 | [5 empty] | PRODUCTION | PAINT | Color No. 4 Sludge | Sludge Consolidator Pump PALIN | Pump Motor | MOTOR | PUMP |  |  | 1 | 2 | 87.05% | 3.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
291 | [5 empty] | PRODUCTION | PAINT | #4 & #5 Tack-Off | ASH #4 | Supply Fan | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 36.7689 | 36.7689 | 105894.414 | 158841.621 | 361.3266 | 541.9898 | [11 empty] | 105894.414 | 158841.621
292 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 5 | Booth No. 5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP11-1 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
293 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 5 | Booth No. 5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP11-2 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
294 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 5 | Booth No. 5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP11-3 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
295 | [5 empty] | PRODUCTION | PAINT | Color Booth No. 5 | Booth No. 5 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP11-4 | 1 | 40 | 89.25% | 49 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 20.0605 | 20.0605 | 57774.2521 | 86661.3782 | 197.1338 | 295.7008 | [11 empty] | 57774.2521 | 86661.3782
296 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Supply Fan # 4 | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 36.7689 | 36.7689 | 105894.414 | 158841.621 | 361.3266 | 541.9898 | [11 empty] | 105894.414 | 158841.621
297 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Supply Fan # 5 | MOTOR | FAN |  |  | 1 | 60 | 91.3% | 72 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 36.7689 | 36.7689 | 105894.414 | 158841.621 | 361.3266 | 541.9898 | [11 empty] | 105894.414 | 158841.621
298 | [5 empty] | PRODUCTION | PAINT | Color No. 5 Sludge | Sludge Pump No. 1 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
299 | [5 empty] | PRODUCTION | PAINT | Color No. 5 Sludge | Sludge Pump No. 2 | Pump Motor | MOTOR | PUMP |  |  | 1 | 20 | 89.7% | 27 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
300 | [5 empty] | PRODUCTION | PAINT | Color No. 5 Sludge | Sludge Consolidator Pump PALIN | Pump Motor | MOTOR | PUMP |  |  | 1 | 2 | 87.05% | 3.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.0284 | 1.0284 | 2961.7186 | 4442.5778 | 10.1058 | 15.1587 | [11 empty] | 2961.7186 | 4442.5778
301 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Infrared Zone #1 | IR Oven | OVEN | IR |  | Electric Infrared Heating Oven | 1 | 0 |  | 55 |  | 3 | 480 | [6 empty] | V | NO | 8760 | 50% | 82.19% | 100% | 100% | 2880 | 4320 | 20.5762 | 20.5762 | 59259.3408 | 88889.0112 | 202.2012 | 303.3018 | [11 empty] | 59259.3408 | 88889.0112
302 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Infrared Zone #2 | IR Oven | OVEN | IR |  | Electric Infrared Heating Oven | 1 | 0 |  | 55 |  | 3 | 480 | [6 empty] | V | NO | 8760 | 50% | 82.19% | 100% | 100% | 2880 | 4320 | 20.5762 | 20.5762 | 59259.3408 | 88889.0112 | 202.2012 | 303.3018 | [11 empty] | 59259.3408 | 88889.0112
303 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Infrared Zone #3 | IR Oven | OVEN | IR |  | Electric Infrared Heating Oven | 1 | 0 |  | 55 |  | 3 | 480 | [6 empty] | V | NO | 8760 | 50% | 82.19% | 100% | 100% | 2880 | 4320 | 20.5762 | 20.5762 | 59259.3408 | 88889.0112 | 202.2012 | 303.3018 | [11 empty] | 59259.3408 | 88889.0112
304 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 | Entrance Air Seal Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
305 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Radiant) | Supply Fan | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 24.7 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
306 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Radiant) | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 0.75 | 87.05% | 1.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.48205 | 0.48205 | 1388.3056 | 2082.4584 | 4.7371 | 7.1056 | [11 empty] | 1388.3056 | 2082.4584
307 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Radiant) | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 1 | 87.05% | 2 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 0.51419 | 0.51419 | 1480.8593 | 2221.2889 | 5.0529 | 7.5793 | [11 empty] | 1480.8593 | 2221.2889
308 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 | Exhaust Fan | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
309 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Convection) | Supply Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
310 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1(Convection) | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 0.75 | 87.05% | 1.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.48205 | 0.48205 | 1388.3056 | 2082.4584 | 4.7371 | 7.1056 | [11 empty] | 1388.3056 | 2082.4584
311 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Convection) | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
312 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Convection) | Recirculating Fan #2 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
313 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Convection) | Recirculating Fan #3 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
314 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Convection) | Recirculating Fan #4 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
315 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 | Exit Air Seal Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
316 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 | Entrance Air Seal Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
317 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Radiant) | Supply Fan | MOTOR | FAN |  |  | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 7.6426 | 7.6426 | 22010.609 | 33015.9135 | 75.1033 | 112.6549 | [11 empty] | 22010.609 | 33015.9135
318 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Radiant) | Combustion Blower | MOTOR | FAN |  |  | 1 | 0.75 | 87.05% | 1.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.48205 | 0.48205 | 1388.3056 | 2082.4584 | 4.7371 | 7.1056 | [11 empty] | 1388.3056 | 2082.4584
319 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Radiant) | Exhaust Fan | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
320 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Convection) | Supply Fan | MOTOR | FAN |  |  | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 9.5532 | 9.5532 | 27513.2612 | 41269.8919 | 93.8791 | 140.8186 | [11 empty] | 27513.2612 | 41269.8919
321 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Convection) | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 0.75 | 87.05% | 1.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.48205 | 0.48205 | 1388.3056 | 2082.4584 | 4.7371 | 7.1056 | [11 empty] | 1388.3056 | 2082.4584
322 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Convection) | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 2 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
323 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Convection) | Recirculating Fan #2 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
324 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Convection) | Recirculating Fan #3 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
325 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 | Exit Air Seal Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
326 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Cooling Tunnel | Supply Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
327 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Cooling Tunnel | Recirculating Fan #1 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
328 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Cooling Tunnel | Recirculating Fan #2 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
329 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Cooling Tunnel | Recirculating Fan #3 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
330 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Cooling Tunnel | Recirculating Fan #4 | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
331 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Cooling Tunnel | Exhaust Fan | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
332 | [5 empty] | PRODUCTION | PAINT | Booth #6 | ASH #6 | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% | 88 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 46.0368 | 46.0368 | 132585.8475 | 198878.7713 | 452.4015 | 678.6022 | [11 empty] | 132585.8475 | 198878.7713
333 | [5 empty] | PRODUCTION | PAINT | Booth #6 | ASH #6 | Supply Fan | MOTOR | FAN |  |  | 1 | 75 | 91.15% | 88 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 46.0368 | 46.0368 | 132585.8475 | 198878.7713 | 452.4015 | 678.6022 | [11 empty] | 132585.8475 | 198878.7713
334 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 6 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP25-1 | 1 | 20 | 89.7% | 24.7 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
335 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 6 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP25-2 | 1 | 20 | 89.7% | 24.7 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
336 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 6 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP25-3 | 1 | 20 | 89.7% | 24.7 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
337 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 6 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP25-4 | 1 | 20 | 89.7% | 24.7 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
338 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 6 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP25-5 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
339 | [5 empty] | PRODUCTION | PAINT | #6 Tack & Flash-Off | ASH #7 | Supply Fan | MOTOR | FAN |  |  | 1 | 50 | 89.25% | 62 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 31.3445 | 31.3445 | 90272.2689 | 135408.4034 | 308.0216 | 462.0324 | [11 empty] | 90272.2689 | 135408.4034
340 | [5 empty] | PRODUCTION | PAINT | Booth #7 & Tack-Off | ASH #8 | Supply Fan | MOTOR | FAN |  |  | 1 | 100 | 91.65% | 113 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 61.0475 | 61.0475 | 175816.6939 | 263725.0409 | 599.9112 | 899.8668 | [11 empty] | 175816.6939 | 263725.0409
341 | [5 empty] | PRODUCTION | PAINT | Booth #7 & Tack-Off | ASH #8 | Supply Fan | MOTOR | FAN |  |  | 1 | 100 | 91.65% | 113 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 61.0475 | 61.0475 | 175816.6939 | 263725.0409 | 599.9112 | 899.8668 | [11 empty] | 175816.6939 | 263725.0409
342 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 7 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP26-1 | 1 | 20 | 89.7% | 24.3 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
343 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 7 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP26-2 | 1 | 20 | 89.7% | 24.3 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
344 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 7 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP26-3 | 1 | 20 | 89.7% | 24.3 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
345 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 7 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP26-4 | 1 | 20 | 89.7% | 24.3 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
346 | [5 empty] | PRODUCTION | PAINT | Plastic | Booth No. 7 | Exhaust Fan | MOTOR | FAN |  | Emission Point EP26-5 | 1 | 10 | 87.05% | 12 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
347 | [5 empty] | PRODUCTION | PAINT | Plastics Parts Booth | Plastics Parts Booth Exhaust | Exhaust Fan | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 24.3 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
348 | [5 empty] | PRODUCTION | PAINT | Plastics Parts Booth | Plastics Parts Booth Exhaust | Exhaust Fan | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 24.3 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
349 | [5 empty] | PRODUCTION | PAINT | Plastics Parts Booth | Plastics Parts Booth Exhaust | Exhaust Fan | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 24.3 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
350 | [5 empty] | PRODUCTION | PAINT | Plastics Parts Booth | Plastics Parts Booth Exhaust | Exhaust Fan | MOTOR | FAN |  |  | 1 | 20 | 89.7% | 24.3 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 9.9799 | 9.9799 | 28742.2074 | 43113.311 | 98.0724 | 147.1087 | [11 empty] | 28742.2074 | 43113.311
351 | [5 empty] | PRODUCTION | PAINT | Booth No. 6 & 7 Plastic | Booth No. 6 & 7 Flash-Off | Exhaust Fan | MOTOR | FAN |  | Emission Point EP27-1 | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 5.1419 | 5.1419 | 14808.5928 | 22212.8891 | 50.529 | 75.7935 | [11 empty] | 14808.5928 | 22212.8891
352 | [5 empty] | PRODUCTION | PAINT | Multi Color Oven | Multi Color Oven Entrance | Entrance Air Seal Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
353 | [5 empty] | PRODUCTION | PAINT | Multi Color Oven | Multi Color Oven | Supply Fan | MOTOR | FAN |  |  | 1 | 15 | 87.85% | 21 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 7.6426 | 7.6426 | 22010.609 | 33015.9135 | 75.1033 | 112.6549 | [11 empty] | 22010.609 | 33015.9135
354 | [5 empty] | PRODUCTION | PAINT | Multi Color Oven | Multi Color Oven | Exhaust Fan | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
355 | [5 empty] | PRODUCTION | PAINT | Multi Color Oven | Multi Color Oven | Combustion Blower | MOTOR | COMB BLOWER |  |  | 1 | 0.75 | 87.05% | 1.4 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 75% | 75% | 2880 | 4320 | 0.48205 | 0.48205 | 1388.3056 | 2082.4584 | 4.7371 | 7.1056 | [11 empty] | 1388.3056 | 2082.4584
356 | [5 empty] | PRODUCTION | PAINT | Multi Color Oven | Multi Color Oven Exit | Exit Air Seal Fan | MOTOR | FAN |  |  | 1 | 7.5 | 87.05% | 10 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 3.8564 | 3.8564 | 11106.4446 | 16659.6669 | 37.8967 | 56.8451 | [11 empty] | 11106.4446 | 16659.6669
357 | [5 empty] | PRODUCTION | PAINT | Multi Color Oven | Cooling Tunnel | Exhaust Fan | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
358 | [5 empty] | PRODUCTION | PAINT | Plastics Oven | Plastics Oven Cooling Tunnel | Recirculation Fan | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
359 | [5 empty] | PRODUCTION | PAINT | Plastics Oven | Plastics Oven Cooling Tunnel | Recirculation Fan | MOTOR | FAN |  |  | 1 | 3 | 87.05% | 4.8 |  | 3 | 480 | [6 empty] | L | NO | 8760 | 100% | 82.19% | 60% | 60% | 2880 | 4320 | 1.5426 | 1.5426 | 4442.5778 | 6663.8667 | 15.1587 | 22.738 | [11 empty] | 4442.5778 | 6663.8667
360 | [5 empty] | FACILITY | HVAC | Paint Mix Room | Heating/Cooling Conditioner | Trane HVAC | MOTOR | PACKAGE UNIT |  |  | 1 | 100 | 94.5% | 65 |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 40% | 95% | 3504 | 5256 | 31.5767 | 74.9947 | 110644.8254 | 394172.1905 | 377.5356 | 1344.9707 | [11 empty] | 110644.8254 | 394172.1905
361 | [5 empty] | PRODUCTION | PAINT | Paint Mix Room | Exhaust Ventilation No. 1 | Trane HVAC | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 60% | 60% | 3504 | 5256 | 5.1419 | 5.1419 | 18017.1212 | 27025.6818 | 61.4769 | 92.2154 | [11 empty] | 18017.1212 | 27025.6818
362 | [5 empty] | PRODUCTION | PAINT | Paint Mix Room | Exhaust Ventilation No. 2 | Trane HVAC | MOTOR | FAN |  |  | 1 | 10 | 87.05% | 14 |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 60% | 60% | 3504 | 5256 | 5.1419 | 5.1419 | 18017.1212 | 27025.6818 | 61.4769 | 92.2154 | [11 empty] | 18017.1212 | 27025.6818
363 | [5 empty] | FACILITY | HVAC |  | 300A | RTU-1 - 13, 15-17 | MOTOR | PACKAGE UNIT |  | Trane PC-37 | 16 | 25 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 32.4348 | 162.1739 | 113651.4783 | 852386.087 | 387.7948 | 2908.4607 |  | 60 | [9 empty] | 113651.4783 | 852386.087
364 | [5 empty] | FACILITY | HVAC |  | 300A | RTU-14 | MOTOR | PACKAGE UNIT |  | Trane PC-07 | 1 | 5 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 33% | 100% | 3504 | 5256 | 1.3379 | 4.0543 | 4688.1235 | 21309.6522 | 15.9965 | 72.7115 |  | 10 | [9 empty] | 4688.1235 | 21309.6522
365 | [5 empty] | FACILITY | HVAC | Multiple | 200, 300, 400 | RTU-18 - RTU-39 | MOTOR | PACKAGE UNIT |  | Trane PC-37 | 22 | 25 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 44.5978 | 222.9891 | 156270.7826 | 1172030.8696 | 533.2178 | 3999.1334 |  | 60 | [9 empty] | 156270.7826 | 1172030.8696
366 | [5 empty] | FACILITY | HVAC |  | 300A Wash Area | RTU-A | MOTOR | PACKAGE UNIT |  | Trane P23N | 1 | 15 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 25% | 100% | 3504 | 5256 | 3.0408 | 12.163 | 10654.8261 | 63928.9565 | 36.3558 | 218.1345 |  | 31 | [9 empty] | 10654.8261 | 63928.9565
367 | [5 empty] | FACILITY | HVAC |  | 300A Electric Room | RTU-B | MOTOR | PACKAGE UNIT |  | Trane P23N | 1 | 15 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 25% | 100% | 3504 | 5256 | 3.0408 | 12.163 | 10654.8261 | 63928.9565 | 36.3558 | 218.1345 |  | 38 | [9 empty] | 10654.8261 | 63928.9565
368 | [5 empty] | FACILITY | HVAC |  | 300D Kitchen | RTU-D | MOTOR | PACKAGE UNIT |  | Trane P18N | 1 | 5 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 33% | 100% | 3504 | 5256 | 1.3379 | 4.0543 | 4688.1235 | 21309.6522 | 15.9965 | 72.7115 |  | 22 | [9 empty] | 4688.1235 | 21309.6522
369 | [5 empty] | FACILITY | HVAC |  | 300D Dining | RTU-E | MOTOR | PACKAGE UNIT |  | Trane P23N | 1 | 10 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 33% | 100% | 3504 | 5256 | 2.6759 | 8.1087 | 9376.247 | 42619.3043 | 31.9931 | 145.423 |  | 38 | [9 empty] | 9376.247 | 42619.3043
370 | [5 empty] | FACILITY | HVAC |  | 300D Locker | RTU-F | MOTOR | PACKAGE UNIT |  | Trane P18N | 1 | 5 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 33% | 100% | 3504 | 5256 | 1.3379 | 4.0543 | 4688.1235 | 21309.6522 | 15.9965 | 72.7115 |  | 25 | [9 empty] | 4688.1235 | 21309.6522
371 | [5 empty] | FACILITY | HVAC |  | 300D Health | RTU-G | MOTOR | PACKAGE UNIT |  | Trane P07N | 1 | 2 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 33% | 100% | 3504 | 5256 | 0.53517 | 1.6217 | 1875.2494 | 8523.8609 | 6.3986 | 29.0846 |  | 5 | [9 empty] | 1875.2494 | 8523.8609
372 | [5 empty] | FACILITY | HVAC | Cab Paint | 400B | RTU-40 - RTU-43 | MOTOR | PACKAGE UNIT |  | Trane PC-37 | 4 | 25 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 8.1087 | 40.5435 | 28412.8696 | 213096.5217 | 96.9487 | 727.1152 |  | 60 | [9 empty] | 28412.8696 | 213096.5217
373 | [5 empty] | FACILITY | HVAC | Cab Paint | 400B | RTU-44- RTU-49 | MOTOR | PACKAGE UNIT |  | Trane PC-37 | 6 | 25 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 12.163 | 60.8152 | 42619.3043 | 319644.7826 | 145.423 | 1090.6727 |  | 60 | [9 empty] | 42619.3043 | 319644.7826
374 | [5 empty] | FACILITY | HVAC |  | 600B | RTU-50 | MOTOR | PACKAGE UNIT |  | Trane PCC-17 | 1 | 7.5 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 33% | 100% | 3504 | 5256 | 2.0069 | 6.0815 | 7032.1852 | 31964.4783 | 23.9948 | 109.0673 |  | 32 | [9 empty] | 7032.1852 | 31964.4783
375 | [5 empty] | FACILITY | HVAC | Multiple | 200, 300, 400 | RTU-51 - RTU-63 | MOTOR | PACKAGE UNIT |  | Trane PC-37 | 13 | 25 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 26.3533 | 131.7663 | 92341.8261 | 692563.6957 | 315.0832 | 2363.1243 |  | 60 | [9 empty] | 92341.8261 | 692563.6957
376 | [5 empty] | FACILITY | HVAC |  | 600A PMIA | RTU-J | MOTOR | PACKAGE UNIT |  | Trane PCC-18 | 1 | 10 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 33% | 100% | 3504 | 5256 | 2.6759 | 8.1087 | 9376.247 | 42619.3043 | 31.9931 | 145.423 |  | 23 | [9 empty] | 9376.247 | 42619.3043
377 | [5 empty] | FACILITY | HVAC |  | 600A Offices | RTU-K | MOTOR | PACKAGE UNIT |  | Trane PCC-37 | 1 | 15 | 92% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 25% | 100% | 3504 | 5256 | 3.0408 | 12.163 | 10654.8261 | 63928.9565 | 36.3558 | 218.1345 |  | 43 | [9 empty] | 10654.8261 | 63928.9565
378 | [5 empty] | FACILITY | HVAC |  |  | UH-2 - UH-5 | MOTOR | PACKAGE UNIT |  | Trane GPND-010ADD1000-NG Unit Heater (FAN) | 4 | 0.05 | 80% |  |  | 1 | 120 | [6 empty] | B | YES | 8760 | 100% | 100% | 80% | 0% | 3504 | 5256 | 0.1492 | 0 | 522.7968 | 0 | 1.7839 | 0 | [11 empty] | 522.7968 | 0
379 | [5 empty] | FACILITY | HVAC |  | Elev. Mach. Rm. | UH-6 | MOTOR | PACKAGE UNIT |  | Chromalox LUH-02-21-Unit Heater (FAN) | 1 | 0.025 | 80% |  |  | 1 | 240 | [6 empty] | B | YES | 8760 | 100% | 100% | 80% | 0% | 3504 | 5256 | 0.01865 | 0 | 65.3496 | 0 | 0.22298 | 0 | [11 empty] | 65.3496 | 0
380 | [5 empty] | FACILITY | HVAC |  | Elev. Mach. Rm. | UH-6 | HEAT | ELECTRIC |  | Chromalox LUH-02-21-Unit Heater (Heat Elements) | 1 | 0 |  |  |  | 1 | 240 | [6 empty] | B | YES | 8760 | 100% | 100% | 80% | 0% | 3504 | 5256 | 2.08 | 0 | 7288.32 | 0 | 24.8688 | 0 |  |  |  |  | 2.6 | [6 empty] | 7288.32 | 0
381 | [5 empty] | FACILITY | BOILER | Office | Office | Boiler No.1 | MOTOR | COMB BLOWER |  | Office Boiler, Electrical Loads | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 51.37% | 100% | 80% | 1800 | 2700 | 0.90424 | 0.72339 | 1627.6364 | 1953.1636 | 5.5537 | 6.6645 | [11 empty] | 1627.6364 | 1953.1636
382 | [5 empty] | FACILITY | BOILER |  | Boiler Room | Boiler No.3 | MOTOR | COMB BLOWER |  | Boiler Room 400A, Electrical Loads | 1 | 7.5 | 89.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 51.37% | 100% | 80% | 1800 | 2700 | 6.2514 | 5.0011 | 11252.514 | 13503.0168 | 38.3952 | 46.0742 | [11 empty] | 11252.514 | 13503.0168
383 | [5 empty] | FACILITY | BOILER |  | Hood Paint Center | Boiler No.4 | MOTOR | COMB BLOWER |  | Hood paint center, Electrical Loads | 1 | 5 | 87.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 51.37% | 100% | 80% | 1800 | 2700 | 4.2629 | 3.4103 | 7673.1429 | 9207.7714 | 26.1818 | 31.4182 | [11 empty] | 7673.1429 | 9207.7714
384 | [5 empty] | FACILITY | BOILER |  | Mechanical Room | Boiler No.5 | MOTOR | COMB BLOWER |  | Main Boiler, Mechanical Room, Electrical Loads | 1 | 40 | 93% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 29% | 50% | 33% | 1016.16 | 1524.24 | 16.043 | 10.5884 | 16302.2658 | 16139.2431 | 55.6256 | 55.0694 | [11 empty] | 16302.2658 | 16139.2431
385 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Exist. CHW Tertiary | P-1 | MOTOR | PUMP |  | Weinman 6L1 | 1 | 100 | 94.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 78.9418 | 78.9418 | 276612.0635 | 414918.0952 | 943.8391 | 1415.7586 | [11 empty] | 276612.0635 | 414918.0952
386 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Existing Cond. W. | P-2 | MOTOR | PUMP |  | Weinman 10L3 | 1 | 75 | 94.1% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 59.458 | 59.458 | 208340.9139 | 312511.3709 | 710.8884 | 1066.3325 | [11 empty] | 208340.9139 | 312511.3709
387 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Exist. CHW Tertiary | P-3 | MOTOR | PUMP |  | Weinman 6L1 | 1 | 100 | 94.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 78.9418 | 78.9418 | 276612.0635 | 414918.0952 | 943.8391 | 1415.7586 | [11 empty] | 276612.0635 | 414918.0952
388 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Existing Cond. W. | P-4 | MOTOR | PUMP |  | Weinman 10L3 | 1 | 75 | 94.1% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 59.458 | 59.458 | 208340.9139 | 312511.3709 | 710.8884 | 1066.3325 | [11 empty] | 208340.9139 | 312511.3709
389 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Exist. HW Tertiary | P-5 | MOTOR | PUMP |  | Weinman 3GB | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
390 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | CHW Primary | P-6 | MOTOR | PUMP |  | B&G VSC 10X10X13 | 1 | 20 | 91% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 75% | 100% | 100% | 2628 | 3942 | 16.3956 | 16.3956 | 43087.6484 | 64631.4725 | 147.0211 | 220.5316 | [11 empty] | 43087.6484 | 64631.4725
391 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | CHW Primary | P-7 | MOTOR | PUMP |  | B&G VSC 10X10X13 | 1 | 20 | 91% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 16.3956 | 16.3956 | 57450.1978 | 86175.2967 | 196.0281 | 294.0422 | [11 empty] | 57450.1978 | 86175.2967
392 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | CHW Primary | P-8 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
393 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | CHW Primary | P-9 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
394 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | CHW Primary | P-10 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
395 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Condenser Water | P-11 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -3/4 | 1 | 125 | 94.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 98.6772 | 98.6772 | 345765.0794 | 518647.619 | 1179.7989 | 1769.6983 | [11 empty] | 345765.0794 | 518647.619
396 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Condenser Water | P-12 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -3/4 | 1 | 125 | 94.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 98.6772 | 98.6772 | 345765.0794 | 518647.619 | 1179.7989 | 1769.6983 | [11 empty] | 345765.0794 | 518647.619
397 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Condenser Water | P-13 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -3/4 | 1 | 125 | 94.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 98.6772 | 98.6772 | 345765.0794 | 518647.619 | 1179.7989 | 1769.6983 | [11 empty] | 345765.0794 | 518647.619
398 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Secondary CHW | P-14 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
399 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Secondary CHW | P-15 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
400 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Secondary CHW | P-16 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
401 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Secondary CHW | P-17 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
402 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Tertiary CHW | P-18 | MOTOR | PUMP |  | B&G VSC 10X10X13 | 1 | 150 | 95% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 11.7789 | 58.8947 | 41273.4316 | 309550.7368 | 140.8307 | 1056.2305 | [11 empty] | 41273.4316 | 309550.7368
403 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Tertiary CHW | P-19 | MOTOR | PUMP |  | B&G VSC 10X10X13 | 1 | 150 | 95% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 11.7789 | 58.8947 | 41273.4316 | 309550.7368 | 140.8307 | 1056.2305 | [11 empty] | 41273.4316 | 309550.7368
404 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Tertiary CW | P-20 | MOTOR | PUMP |  | B&G VSC 10X10X13L | 1 | 200 | 95% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 15.7053 | 78.5263 | 55031.2421 | 412734.3158 | 187.7743 | 1408.3073 | [11 empty] | 55031.2421 | 412734.3158
405 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Tertiary CW | P-21 | MOTOR | PUMP |  | B&G VSC 10X10X13L | 1 | 200 | 95% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 15.7053 | 78.5263 | 55031.2421 | 412734.3158 | 187.7743 | 1408.3073 | [11 empty] | 55031.2421 | 412734.3158
406 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Primary HW | P-22 | MOTOR | PUMP |  | B&G 1510 4AC | 1 | 5 | 87.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 4.2629 | 4.2629 | 14937.0514 | 22405.5771 | 50.9673 | 76.451 | [11 empty] | 14937.0514 | 22405.5771
407 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Primary HW | P-23 | MOTOR | PUMP |  | B&G 1510 6E | 1 | 15 | 91% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 12.2967 | 12.2967 | 43087.6484 | 64631.4725 | 147.0211 | 220.5316 | [11 empty] | 43087.6484 | 64631.4725
408 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Secondary HW | P-24 | MOTOR | PUMP |  | B&G 1510 5BC | 1 | 7.5 | 89.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 6.2514 | 6.2514 | 21904.8939 | 32857.3408 | 74.7426 | 112.1138 | [11 empty] | 21904.8939 | 32857.3408
409 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Secondary HW | P-25 | MOTOR | PUMP |  | B&G 1510 5BC | 1 | 7.5 | 89.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 6.2514 | 6.2514 | 21904.8939 | 32857.3408 | 74.7426 | 112.1138 | [11 empty] | 21904.8939 | 32857.3408
410 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Secondary HW | P-26 | MOTOR | PUMP |  | B&G 1510 5BC | 1 | 7.5 | 89.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 6.2514 | 6.2514 | 21904.8939 | 32857.3408 | 74.7426 | 112.1138 | [11 empty] | 21904.8939 | 32857.3408
411 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Tertiary HW | P-27 | MOTOR | PUMP |  | B&G 1510 6G | 1 | 50 | 93% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 40.1075 | 40.1075 | 140536.7742 | 210805.1613 | 479.5311 | 719.2967 | [11 empty] | 140536.7742 | 210805.1613
412 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | CHW Primary | P-28 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
413 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Condenser Water | P-29 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -3/4L | 1 | 125 | 94.5% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 98.6772 | 98.6772 | 345765.0794 | 518647.619 | 1179.7989 | 1769.6983 | [11 empty] | 345765.0794 | 518647.619
414 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Secondary CHW | P-30 | MOTOR | PUMP |  | B&G VSCS 12X14X12 -1/2 | 1 | 25 | 92.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 20.184 | 20.184 | 70724.6753 | 106087.013 | 241.3225 | 361.9837 | [11 empty] | 70724.6753 | 106087.013
415 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Tertiary CW | P-31 | MOTOR | PUMP |  | B&G VSC 10X10X13L | 1 | 200 | 95% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 15.7053 | 78.5263 | 55031.2421 | 412734.3158 | 187.7743 | 1408.3073 | [11 empty] | 55031.2421 | 412734.3158
416 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | Main Bldg. HW Tertiary | P-32 | MOTOR | PUMP |  | B&G 1510 3G | 1 | 20 | 91.4% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 16.3239 | 16.3239 | 57198.7746 | 85798.1619 | 195.1702 | 292.7553 | [11 empty] | 57198.7746 | 85798.1619
417 | [5 empty] | FACILITY | PUMPING | Facility Pumping-Site Wide | 400 Bld. HW Tertiary | P-33 | MOTOR | PUMP |  | B&G 1510 6G | 1 | 50 | 93% |  |  | 3 | 480 | [6 empty] | B | YES | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 40.1075 | 40.1075 | 140536.7742 | 210805.1613 | 479.5311 | 719.2967 | [11 empty] | 140536.7742 | 210805.1613
418 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Comb. Air 150 HP.B | SF-3 | MOTOR | FAN |  | Greenheck LSF-12 Supply Fan | 1 | 0.33333 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.31083 | 0.31083 | 1089.16 | 1633.74 | 3.7164 | 5.5745 | [11 empty] | 1089.16 | 1633.74
419 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Comb. Air 800 HP.B | SF-4 | MOTOR | FAN |  | Greenheck LSF-18 Supply Fan | 1 | 2 | 84% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 1.7762 | 1.7762 | 6223.7714 | 9335.6571 | 21.2364 | 31.8546 | [11 empty] | 6223.7714 | 9335.6571
420 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Wabco Bldg. | SF-5 | MOTOR | FAN |  | Greenheck RSF-200 Supply Fan | 1 | 3 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 2.5577 | 2.5577 | 8962.2309 | 13443.3463 | 30.5804 | 45.8706 | [11 empty] | 8962.2309 | 13443.3463
421 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 500 Bldg. | SF-6 | MOTOR | FAN |  | Greenheck LSF-30 Supply Fan | 1 | 3 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 2.5577 | 2.5577 | 8962.2309 | 13443.3463 | 30.5804 | 45.8706 | [11 empty] | 8962.2309 | 13443.3463
422 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300A Bldg. | SF-7 | MOTOR | FAN |  | Greenheck LSF-16 Supply Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
423 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300A Bldg. | SF-8 | MOTOR | FAN |  | Greenheck LSF-15 Supply Fan | 1 | 0.5 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.46625 | 0.46625 | 1633.74 | 2450.61 | 5.5745 | 8.3618 | [11 empty] | 1633.74 | 2450.61
424 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Dyno 2 Bldg. | SF-9 | MOTOR | FAN |  | Greenheck RSF-200 Supply Fan | 1 | 3 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 2.5577 | 2.5577 | 8962.2309 | 13443.3463 | 30.5804 | 45.8706 | [11 empty] | 8962.2309 | 13443.3463
425 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Align. Bldg. | SF-10 | MOTOR | FAN |  | Greenheck LSF-30 Supply Fan | 1 | 5 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 4.2629 | 4.2629 | 14937.0514 | 22405.5771 | 50.9673 | 76.451 | [11 empty] | 14937.0514 | 22405.5771
426 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Align. Bldg. | SF-11, SF11A | MOTOR | FAN |  | Greenheck LSF-30 Supply Fan | 1 | 5 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 4.2629 | 4.2629 | 14937.0514 | 22405.5771 | 50.9673 | 76.451 | [11 empty] | 14937.0514 | 22405.5771
427 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 500B Bldg. | SF-12 | MOTOR | FAN |  | Greenheck LSF-24 Supply Fan | 1 | 2 | 84% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 1.7762 | 1.7762 | 6223.7714 | 9335.6571 | 21.2364 | 31.8546 | [11 empty] | 6223.7714 | 9335.6571
428 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Toilets 900 Bldg. | EF-6 | MOTOR | FAN |  | Greenheck GB-120 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
429 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Machine Room | EF-7 | MOTOR | FAN |  | Greenheck GB-420-10 Exhaust Fan | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
430 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Machine Room | EF-8 | MOTOR | FAN |  | Greenheck GB-420-10 Exhaust Fan | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
431 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Machine Room | EF-9 | MOTOR | FAN |  | Greenheck GB-420-10 Exhaust Fan | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
432 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Wabco Bldg. | EF-10, EF-11 | MOTOR | FAN |  | Greenheck GB-200-15 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
433 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 500 Bldg. | EF-12 | MOTOR | FAN |  | Greenheck GB-480 Exhaust Fan | 1 | 3 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 2.5577 | 2.5577 | 8962.2309 | 13443.3463 | 30.5804 | 45.8706 | [11 empty] | 8962.2309 | 13443.3463
434 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200 Bldg. | EF-13 | MOTOR | FAN |  | Greenheck GB-90-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
435 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200 Bldg. | EF-14 | MOTOR | FAN |  | Greenheck GB-90-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
436 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200 Bldg. | EF-15 | MOTOR | FAN |  | Greenheck SP-158 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
437 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200 Bldg. Comp Rm | EF-16 | MOTOR | FAN |  | Greenheck GB-300-5 Exhaust Fan | 1 | 0.5 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.46625 | 0.46625 | 1633.74 | 2450.61 | 5.5745 | 8.3618 | [11 empty] | 1633.74 | 2450.61
438 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300A Bldg. | EF-17 | MOTOR | FAN |  | Greenheck GB-220-7 Exhaust Fan | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
439 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300A Bldg. | EF-18 | MOTOR | FAN |  | Greenheck GB-180-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
440 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 500 Bldg. Comp. Rm | EF-19 | MOTOR | FAN |  | Greenheck SPF-24 Exhaust Fan | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
441 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200B SW. Gear | EF-20 | MOTOR | FAN |  | Greenheck GB-300-10 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
442 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200 Substation #5 | EF-21 | MOTOR | FAN |  | Greenheck GB-300-10 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
443 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 700 Tun./Brdg | EF-22, EF-22A | MOTOR | FAN |  | Greenheck GB-420-7 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
444 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300D Dishwash | EF-23 | MOTOR | FAN |  | Greenheck GB-220-3 Exhaust Fan | 1 | 0.33333 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.31083 | 0.31083 | 1089.16 | 1633.74 | 3.7164 | 5.5745 | [11 empty] | 1089.16 | 1633.74
445 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300D Janitor | EF-24 | MOTOR | FAN |  | Greenheck G-60-D Exhaust Fan | 1 | 0.016667 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.015542 | 0.015542 | 54.458 | 81.687 | 0.18582 | 0.27873 | [11 empty] | 54.458 | 81.687
446 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300D Hlth. Tlt. | EF-25 | MOTOR | FAN |  | Greenheck SP-117 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
447 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300D Lckr. Rm. | EF-26 | MOTOR | FAN |  | Greenheck GB-100-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
448 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400B Comp. Rm. | EF-27 | MOTOR | FAN |  | Greenheck GWB-21-5 Exhaust Fan | 1 | 0.5 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.46625 | 0.46625 | 1633.74 | 2450.61 | 5.5745 | 8.3618 | [11 empty] | 1633.74 | 2450.61
449 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400B Toilets | EF-28 | MOTOR | FAN |  | Greenheck GWB-24-5 Exhaust Fan | 1 | 0.5 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.46625 | 0.46625 | 1633.74 | 2450.61 | 5.5745 | 8.3618 | [11 empty] | 1633.74 | 2450.61
450 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400B Toilets | EF-29 | MOTOR | FAN |  | Greenheck GWB-14-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
451 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400A SW. Gear | EF-30 | MOTOR | FAN |  | Greenheck GWB-24-7 Exhaust Fan | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
452 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400A Toilet | EF-31 | MOTOR | FAN |  | Greenheck GB-130-3 Exhaust Fan | 1 | 0.33333 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.31083 | 0.31083 | 1089.16 | 1633.74 | 3.7164 | 5.5745 | [11 empty] | 1089.16 | 1633.74
453 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400A Bldg. | EF-32, EF-32A | MOTOR | FAN |  | Greenheck RPBE-60-H Exhaust Fan | 1 | 3 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 2.5577 | 2.5577 | 8962.2309 | 13443.3463 | 30.5804 | 45.8706 | [11 empty] | 8962.2309 | 13443.3463
454 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400A Bldg. | EF-33 | MOTOR | FAN |  | Greenheck RPBE-60-H Exhaust Fan | 1 | 3 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 2.5577 | 2.5577 | 8962.2309 | 13443.3463 | 30.5804 | 45.8706 | [11 empty] | 8962.2309 | 13443.3463
455 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400B Bldg. | EF-34 | MOTOR | FAN |  | Greenheck GWB-24-7 Exhaust Fan | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
456 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400B Paint Mix | EF-35 | MOTOR | FAN |  | Greenheck GWB-24-20 Exhaust Fan | 1 | 2 | 84% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 1.7762 | 1.7762 | 6223.7714 | 9335.6571 | 21.2364 | 31.8546 | [11 empty] | 6223.7714 | 9335.6571
457 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400B Paint Mix | EF-36 | MOTOR | FAN |  | Greenheck GWB-18-5 Exhaust Fan | 1 | 0.5 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.46625 | 0.46625 | 1633.74 | 2450.61 | 5.5745 | 8.3618 | [11 empty] | 1633.74 | 2450.61
458 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Elev. Mach. Rm. | EF-37 | MOTOR | FAN |  | Greenheck SDE-16-24-B Exhaust Fan | 1 | 0.16667 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.15542 | 0.15542 | 544.58 | 816.87 | 1.8582 | 2.7873 | [11 empty] | 544.58 | 816.87
459 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400A Fut. Comp. | EF-38 | MOTOR | FAN |  | Greenheck GWB-14-3 Exhaust Fan | 1 | 0.33333 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.31083 | 0.31083 | 1089.16 | 1633.74 | 3.7164 | 5.5745 | [11 empty] | 1089.16 | 1633.74
460 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Dyno 2 Bldg. | EF-39, EF-40 | MOTOR | FAN |  | Greenheck GB-200-15 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
461 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400C Bldg. | EF-41 | MOTOR | FAN |  | Greenheck GB-540-30 Exhaust Fan | 1 | 3 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 2.5577 | 2.5577 | 8962.2309 | 13443.3463 | 30.5804 | 45.8706 | [11 empty] | 8962.2309 | 13443.3463
462 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 400A Storage | EF-42 | MOTOR | FAN |  | Greenheck GWB-A-3 Exhaust Fan | 1 | 0.33333 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.31083 | 0.31083 | 1089.16 | 1633.74 | 3.7164 | 5.5745 | [11 empty] | 1089.16 | 1633.74
463 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Align. Bldg. | EF-43 | MOTOR | FAN |  | Greenheck GB-360-3 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
464 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Align. Bldg. | EF-44 | MOTOR | FAN |  | Greenheck GB-360-3 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
465 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 500D Alignment | EF-45, EF-45A | MOTOR | FAN |  | Greenheck GB-480-30 Exhaust Fan | 1 | 3 | 87.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 2.5577 | 2.5577 | 8962.2309 | 13443.3463 | 30.5804 | 45.8706 | [11 empty] | 8962.2309 | 13443.3463
466 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 500B Toilet | EF-46 | MOTOR | FAN |  | Greenheck GB-160-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
467 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 300A Amenities | EF-47 | MOTOR | FAN |  | Greenheck GB-130-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
468 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200D Sw. Gear | EF-48 | MOTOR | FAN |  | Greenheck GB-220-10 Exhaust Fan | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
469 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200D Storage | EF-49 | MOTOR | FAN |  | Greenheck GWB-14-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
470 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | PMIA | EF-50 | MOTOR | FAN |  | Greenheck GB-300-10 Exhaust Fan | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
471 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 600A Bldg. | EF-51 | MOTOR | FAN |  | Greenheck GB-80-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
472 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 600A Bldg. | EF-52 | MOTOR | FAN |  | Greenheck GB-90-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
473 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 200D Amenities | EF-53 | MOTOR | FAN |  | Greenheck GB-160-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
474 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | 600A PMIA | EF-54 | MOTOR | FAN |  | Greenheck GB-160-4 Exhaust Fan | 1 | 0.25 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.23312 | 0.23312 | 816.87 | 1225.305 | 2.7873 | 4.1809 | [11 empty] | 816.87 | 1225.305
475 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Kitchen | MU-1 Exhaust Fan | MOTOR | FAN |  | Carnes VRBK18S1 | 1 | 1 | 82.5% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.90424 | 0.90424 | 3168.4655 | 4752.6982 | 10.8112 | 16.2169 | [11 empty] | 3168.4655 | 4752.6982
476 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Kitchen | MU-2 Exhaust Fan | MOTOR | FAN |  | Carnes VRBK24V1 | 1 | 2 | 84% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 1.7762 | 1.7762 | 6223.7714 | 9335.6571 | 21.2364 | 31.8546 | [11 empty] | 6223.7714 | 9335.6571
477 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Kitchen | MU-1 Makeup Fan | MOTOR | FAN |  | Greasemaster GM-77 | 1 | 0.5 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.46625 | 0.46625 | 1633.74 | 2450.61 | 5.5745 | 8.3618 | [11 empty] | 1633.74 | 2450.61
478 | [5 empty] | FACILITY | EXHAUST | Facility EXH Fans-Site Wide | Kitchen | MU-2 Makeup Fan | MOTOR | FAN |  | Greasemaster GM-77 | 1 | 0.75 | 80% |  |  | 3 | 480 | [6 empty] | B | NO | 8760 | 100% | 100% | 100% | 100% | 3504 | 5256 | 0.69937 | 0.69937 | 2450.61 | 3675.915 | 8.3618 | 12.5427 | [11 empty] | 2450.61 | 3675.915
479 | [5 empty] | FACILITY | COOLING TOWER | Evaporative Cooling Towers | Outside | CT-1 | MOTOR | FAN |  | SPX (Marley) NC8405TAN Cooling Tower | 1 | 40 | 94.1% |  |  | 3 | 480 | [6 empty] | I | YES | 8760 | 100% | 40% | 100% | 100% | 1401.6 | 2102.4 | 31.7109 | 31.7109 | 44446.0616 | 66669.0925 | 151.6562 | 227.4843 |  | 1250 | [9 empty] | 44446.0616 | 66669.0925
480 | [5 empty] | FACILITY | COOLING TOWER | Evaporative Cooling Towers | Outside | CT-2 | MOTOR | FAN |  | SPX (Marley) NC8405TAN Cooling Tower | 1 | 40 | 94.1% |  |  | 3 | 480 | [6 empty] | I | YES | 8760 | 100% | 40% | 100% | 100% | 1401.6 | 2102.4 | 31.7109 | 31.7109 | 44446.0616 | 66669.0925 | 151.6562 | 227.4843 |  | 1250 | [9 empty] | 44446.0616 | 66669.0925
481 | [5 empty] | FACILITY | COOLING TOWER | Evaporative Cooling Towers | Outside | CT-3 | MOTOR | FAN |  | Marley NC-8032 Cooling Tower | 1 | 50 | 93% |  |  | 3 | 480 | [6 empty] | I | YES | 8760 | 100% | 40% | 100% | 100% | 1401.6 | 2102.4 | 40.1075 | 40.1075 | 56214.7097 | 84322.0645 | 191.8125 | 287.7187 |  | 1875 | [9 empty] | 56214.7097 | 84322.0645
482 | [5 empty] | FACILITY | COOLING TOWER | Evaporative Cooling Towers | Outside | CT-4 | MOTOR | FAN |  | Marley NC-8032 Cooling Tower | 1 | 50 | 93% |  |  | 3 | 480 | [6 empty] | I | YES | 8760 | 100% | 40% | 100% | 100% | 1401.6 | 2102.4 | 40.1075 | 40.1075 | 56214.7097 | 84322.0645 | 191.8125 | 287.7187 |  | 1875 | [9 empty] | 56214.7097 | 84322.0645
483 | [5 empty] | FACILITY | COOLING TOWER | Evaporative Cooling Towers | Outside | CT-5 | MOTOR | FAN |  | Marley NC-8032 Cooling Tower | 1 | 50 | 93% |  |  | 3 | 480 | [6 empty] | I | YES | 8760 | 100% | 40% | 100% | 100% | 1401.6 | 2102.4 | 40.1075 | 40.1075 | 56214.7097 | 84322.0645 | 191.8125 | 287.7187 |  | 1875 | [9 empty] | 56214.7097 | 84322.0645
484 | [5 empty] | FACILITY | COOLING TOWER | Evaporative Cooling Towers | Outside | CT-6 | MOTOR | FAN |  | Marley NC-8032 Cooling Tower | 1 | 50 | 93% |  |  | 3 | 480 | [6 empty] | I | YES | 8760 | 100% | 40% | 100% | 100% | 1401.6 | 2102.4 | 40.1075 | 40.1075 | 56214.7097 | 84322.0645 | 191.8125 | 287.7187 |  | 1875 | [9 empty] | 56214.7097 | 84322.0645
485 | [5 empty] | FACILITY | CHILLER | Chillers-Site Wide | Facility Room - BLDG 200 | Chiller-1 | MOTOR | WATER-COOLED |  | Smardt WB400.3UG12 Centrifugal Chiller | 1 | 458 | 95.8% |  |  | 3 | 480 | [6 empty] | V | YES | 8760 | 100% | 100% | 10% | 70% | 3504 | 5256 | 35.6647 | 249.653 | 124969.1724 | 1312176.3106 | 426.4123 | 4477.3293 |  | 1050 | [9 empty] | 124969.1724 | 1312176.3106
486 | [5 empty] | FACILITY | CHILLER | Chillers-Site Wide | Facility Room - BLDG 200 | Chiller-2 | MOTOR | WATER-COOLED |  | Smardt WB400.3UG12 Centrifugal Chiller | 1 | 458 | 95.8% |  |  | 3 | 480 | [6 empty] | V | YES | 8760 | 100% | 100% | 10% | 70% | 3504 | 5256 | 35.6647 | 249.653 | 124969.1724 | 1312176.3106 | 426.4123 | 4477.3293 |  | 1050 | [9 empty] | 124969.1724 | 1312176.3106
487 | [5 empty] | FACILITY | CHILLER | Chillers-Site Wide | Facility Room - BLDG 200 | Chiller-3 | MOTOR | WATER-COOLED |  | Trane CVH1280 Centrifugal Chiller | 1 | 1155.7641 | 95.8% |  |  | 3 | 480 | [6 empty] | V | YES | 8760 | 100% | 100% | 0% | 70% | 3504 | 5256 | 0 | 630 | 0 | 3311280 | 0 | 11298.5509 |  | 1500 | [9 empty] | 0 | 3311280
488 | [5 empty] | FACILITY | CHILLER | Chillers-Site Wide | Facility Room - BLDG 200 | Chiller-4 | MOTOR | WATER-COOLED |  | Trane CVH1280 Centrifugal Chiller | 1 | 1155.7641 | 95.8% |  |  | 3 | 480 | [6 empty] | V | YES | 8760 | 100% | 100% | 0% | 70% | 3504 | 5256 | 0 | 630 | 0 | 3311280 | 0 | 11298.5509 |  | 1500 | [9 empty] | 0 | 3311280
489 | [5 empty] | FACILITY | CHILLER | Chillers-Site Wide | Facility Room - BLDG 200 | Chiller-5 | MOTOR | WATER-COOLED |  | Trane CVH1280 Centrifugal Chiller | 1 | 1155.7641 | 95.8% |  |  | 3 | 480 | [6 empty] | V | YES | 8760 | 100% | 100% | 0% | 0% | 3504 | 5256 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | [9 empty] | 0 | 0
490 | [5 empty] | FACILITY | CHILLER | Chillers-Site Wide | Facility Room - BLDG 200 | Chiller-6 | MOTOR | WATER-COOLED |  | Trane CVH1280 Centrifugal Chiller | 1 | 1155.7641 | 95.8% |  |  | 3 | 480 | [6 empty] | V | YES | 8760 | 100% | 100% | 0% | 0% | 3504 | 5256 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | [9 empty] | 0 | 0
491 | [5 empty] | FACILITY | CHILLER | Chillers-Site Wide | Hood Paint | Air-Cooled Chiller | MOTOR | AIR-COOLED |  | Trane RTAC3504 | 2 | 275 | 95% |  |  | 3 | 480 | [6 empty] | V | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 43.1895 | 215.9474 | 151335.9158 | 1135019.3684 | 516.3793 | 3872.845 |  | 350 | [9 empty] | 151335.9158 | 1135019.3684
492 | [5 empty] | FACILITY | CHILLER | Chillers-Site Wide | Front Office | Air-Cooled Chiller | MOTOR | AIR-COOLED |  | Trane CGAM | 1 | 75 | 94.1% |  |  | 3 | 480 | [6 empty] | V | YES | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 5.9458 | 29.729 | 20834.0914 | 156255.6854 | 71.0888 | 533.1663 |  | 100 | [9 empty] | 20834.0914 | 156255.6854
493 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Compressor #1 | MOTOR | AIR COMPRESSOR |  | Ingersoll-Rand Centac 1CV Centrifugal | 1 | 500 | 95.5% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 100% | 10% | 50% | 3504 | 5256 | 39.0576 | 195.288 | 136857.801 | 1026433.5079 | 466.978 | 3502.3348 | [11 empty] | 136857.801 | 1026433.5079
494 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Compressor #4 | MOTOR | AIR COMPRESSOR |  | IR Model: RS160i-A125 | 1 | 200 | 96.2% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 42% | 75% | 75% | 1471.68 | 2207.52 | 116.3202 | 116.3202 | 171186.0624 | 256779.0936 | 584.1108 | 876.1662 | [11 empty] | 171186.0624 | 256779.0936
495 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Compressor #5 | MOTOR | AIR COMPRESSOR |  | Ingersoll-Rand 200 HP Fixed Speed | 1 | 200 | 95% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 42% | 25% | 25% | 1471.68 | 2207.52 | 39.2632 | 39.2632 | 57782.8042 | 86674.2063 | 197.163 | 295.7445 | [11 empty] | 57782.8042 | 86674.2063
496 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Compressor #9 | MOTOR | AIR COMPRESSOR |  | IR Model: RS160i-A125 | 1 | 200 | 96.2% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 42% | 75% | 75% | 1471.68 | 2207.52 | 116.3202 | 116.3202 | 171186.0624 | 256779.0936 | 584.1108 | 876.1662 | [11 empty] | 171186.0624 | 256779.0936
497 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Compressor #10 | MOTOR | AIR COMPRESSOR |  | Ingersoll-Rand 200 HP Fixed Speed | 1 | 200 | 95% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 42% | 25% | 25% | 1471.68 | 2207.52 | 39.2632 | 39.2632 | 57782.8042 | 86674.2063 | 197.163 | 295.7445 | [11 empty] | 57782.8042 | 86674.2063
498 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Compressor #16 | MOTOR | AIR COMPRESSOR |  | Ingersoll-Rand 100 HP Fixed Speed | 1 | 100 | 94.5% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 42% | 80% | 80% | 1471.68 | 2207.52 | 63.1534 | 63.1534 | 92941.6533 | 139412.48 | 317.1299 | 475.6949 | [11 empty] | 92941.6533 | 139412.48
499 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Compressor #19 | MOTOR | AIR COMPRESSOR |  | Ingersoll-Rand 100 HP VSD | 1 | 100 | 94.5% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 42% | 25% | 25% | 1471.68 | 2207.52 | 19.7354 | 19.7354 | 29044.2667 | 43566.4 | 99.1031 | 148.6547 | [11 empty] | 29044.2667 | 43566.4
500 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Air Dryer | MOTOR | AIR DRYER |  | Ingersoll-Rand 2,000 Scfm NVC2000A Thermal Mass Dryer (for Compressor #9 & #10) | 1 | 18 | 91% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 42% | 100% | 100% | 1471.68 | 2207.52 | 14.756 | 14.756 | 21716.1748 | 32574.2622 | 74.0986 | 111.1479 | [11 empty] | 21716.1748 | 32574.2622
501 | [5 empty] | FACILITY | COMP AIR | Compressed Air-Site Wide | Facility Room | Air Dryer | MOTOR | AIR DRYER |  | Ingersoll-Rand 2,400 Scfm NVC2400A Thermal Mass Dryer (for Compressor #4 & 5) | 1 | 21 | 91% |  |  | 3 | 480 | [6 empty] | V | NO | 8760 | 100% | 42% | 100% | 100% | 1471.68 | 2207.52 | 17.2154 | 17.2154 | 25335.5372 | 38003.3058 | 86.4484 | 129.6726 | [11 empty] | 25335.5372 | 38003.3058
502 | [5 empty] | VEHICLE | CHARGING | Plant Wide | Plant Wide | Lifts and Utility Vehicles | FORKLIFT | ELECTRIC |  | Electric Vehicle with an EIGHT-hour charge time | 187 | 0 |  |  |  | 1 | 277 | [6 empty] | I | NO | 8760 | 75% | 90% | 10% | 50% | 3153.6 | 4730.4 | 106.59 | 532.95 | 336142.224 | 2521066.68 | 1146.9643 | 8602.2325 |  |  | 187 | 7.6 | 1421.2 | [6 empty] | 336142.224 | 2521066.68
503 | [5 empty] | VEHICLE | CHARGING | Plant Wide | Plant Wide | Lifts and Utility Vehicles | FORKLIFT | ELECTRIC |  | Electric Vehicle with an THREE-hour charge time | 20 | 0 |  |  |  | 1 | 277 | [6 empty] | I | NO | 8760 | 100% | 8.562% | 100% | 100% | 300.0125 | 450.0187 | 152 | 152 | 45601.897 | 68402.8454 | 155.6001 | 233.4001 |  |  | 20 | 7.6 | 152 | [6 empty] | 45601.897 | 68402.8454
504 | [5 empty] | FACILITY | LIGHTING | B200 | B200 | LED Fixtures | LIGHT | LED |  | See "NEW LED Lights" tab | 1652 | 0 |  |  |  | 1 | 277 | [6 empty] | L | NO | 8760 | kWh: 226283.568; kWh: 339425.352; MMBTU: 772.1112; MMBTU: 1158.1668 | [11 empty] | 226283.568 | 339425.352
505 | [5 empty] | FACILITY | LIGHTING | B400 | B400 | LED Fixtures | LIGHT | LED |  | See "NEW LED Lights" tab | 1616 | 0 |  |  |  | 1 | 277 | [6 empty] | L | NO | 8760 | kWh: 280386.036; kWh: 420579.054; MMBTU: 956.7164; MMBTU: 1435.0746 | [11 empty] | 280386.036 | 420579.054
506 | [5 empty] | FACILITY | LIGHTING | Audit | Audit | LED Fixtures | LIGHT | LED |  | See "NEW LED Lights" tab | 146 | 0 |  |  |  | 1 | 277 | [6 empty] | L | NO | 8760 | kWh: 5692.624; kWh: 8538.936; MMBTU: 19.424; MMBTU: 29.136 | [11 empty] | 5692.624 | 8538.936
507 | [5 empty] | FACILITY | LIGHTING | Offline | Offline | LED Fixtures | LIGHT | LED |  | See "NEW LED Lights" tab | 1497 | 0 |  |  |  | 1 | 277 | [6 empty] | L | NO | 8760 | kWh: 345958.032; kWh: 518937.048; MMBTU: 1180.4572; MMBTU: 1770.6859 | [11 empty] | 345958.032 | 518937.048
508 | [5 empty] | FACILITY | LIGHTING | PDI | PDI | LED Fixtures | LIGHT | LED |  | See "NEW LED Lights" tab | 696 | 0 |  |  |  | 1 | 277 | [6 empty] | L | NO | 8760 | kWh: 28212.534; kWh: 42318.801; MMBTU: 96.2651; MMBTU: 144.3977 | [11 empty] | 28212.534 | 42318.801
509 | [5 empty] | FACILITY | LIGHTING | Refurb | Refurb | LED Fixtures | LIGHT | LED |  | See "NEW LED Lights" tab | 88 | 0 |  |  |  | 1 | 277 | [6 empty] | L | NO | 8760 | kWh: 2495.178; kWh: 3742.767; MMBTU: 8.5139; MMBTU: 12.7708 | [11 empty] | 2495.178 | 3742.767
510 | [5 empty] | FACILITY | LIGHTING | Training | Training | LED Fixtures | LIGHT | LED |  | See "NEW LED Lights" tab | 400 | 0 |  |  |  | 1 | 277 | [6 empty] | L | NO | 8760 | kWh: 18655.182; kWh: 27982.773; MMBTU: 63.6541; MMBTU: 95.4811 | [11 empty] | 18655.182 | 27982.773
511 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
512 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
513 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
514 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
515 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
516 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
517 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
518 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
519 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
520 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
521 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
522 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
523 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
524 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
525 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
526 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
527 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
528 | [29 empty] | 8760 | DF: 100%; OF: 82.19% | [11 empty] | 0 | 0
| INSERT LINES ONLY - DO NOT DRAG DOWN | [26 empty] | INFO Only | INFO Only |  | Changes kW | Changes Hours | Changes kW | Changes kW |  |  |  | TOTALS | 17917257.9737 | 44177353.0774 | 61136.1926 | 150739.3135 | [11 empty] | 17917257.9737 | 44177353.0774
[31 empty] | kWh: Winter; kWh: Summer; MMBTU: Winter; MMBTU: Summer | [12 empty] | 62094611.0511
[37 empty] | 6045.8774 | 9375.2854 | kWh | kWh | MMBTU | MMBTU
[37 empty] | 0.74822 |  |  | 62094611.0511 |  | 211875.5062
0
CHECKS
The tables below are created manually by sorting the above lines.
These do not update automatically.
The data from the tables below are used to create Energy USE pie charts.
[38 empty] | GROUP | SYSTEM | EQUIPMENT 1 | EQUIPMENT 2 | ELEC EQUIV
[31 empty] | kW: SORT 1; kWh: SORT 2; kWh: SORT 3; MMBTU: SORT 4; MMBTU: MMBTU | # of Line Items
[31 empty] | kW: FACILITY; kWh: BOILER; kWh: COMB BLOWER; MMBTU: COMFORT; MMBTU: 21.2 | 4 | 8%
[31 empty] | kW: FACILITY; kWh: BOILER; kWh: COMB BLOWER; MMBTU: PROCESS; MMBTU: 243.8 | 0 | 92%
[31 empty] | kW: FACILITY; kWh: CHILLER; kWh: MOTOR; MMBTU: AIR COOLED; MMBTU: 4993 | 2
[31 empty] | kW: FACILITY; kWh: CHILLER; kWh: MOTOR; MMBTU: WATER-COOLED; MMBTU: 32405 | 6
[31 empty] | kW: FACILITY; kWh: COMP AIR; kWh: MOTOR; MMBTU: AIR COMPRESSOR; MMBTU: 8916 | 7
[31 empty] | kW: FACILITY; kWh: COMP AIR; kWh: MOTOR; MMBTU: AIR DRYER; MMBTU: 401 | 2
[31 empty] | kW: FACILITY; kWh: COOLING TOWER; kWh: MOTOR; MMBTU: FAN; MMBTU: 2676 | 6
[31 empty] | kW: FACILITY; kWh: EXHAUST; kWh: MOTOR; MMBTU: FAN; MMBTU: 1817 | 61
[31 empty] | kW: FACILITY; kWh: HVAC; kWh: HEAT; MMBTU: ELECTRICAL; MMBTU: 25 | 1
[31 empty] | kW: FACILITY; kWh: HVAC; kWh: MOTOR; MMBTU: PACKAGE UNIT; MMBTU: 15844 | 18
[31 empty] | kW: FACILITY; kWh: LIGHTING; kWh: LIGHT; MMBTU: ALL TYPES; MMBTU: 7743 | 7
[31 empty] | kW: FACILITY; kWh: PUMPING; kWh: MOTOR; MMBTU: PUMP; MMBTU: 38086 | 33
[31 empty] | kW: FACILITY; kWh: WWTP; kWh: MOTOR; MMBTU: PUMP & MIXER; MMBTU: 106 | 10
[31 empty] | kW: PRODUCTION; kWh: PAINT; kWh: MOTOR; MMBTU: COMB BLOWER; MMBTU: 2778 | 38
[31 empty] | kW: PRODUCTION; kWh: PAINT; kWh: MOTOR; MMBTU: FAN; MMBTU: 48014 | 267
[31 empty] | kW: PRODUCTION; kWh: PAINT; kWh: MOTOR; MMBTU: PUMP; MMBTU: 4548 | 37
[31 empty] | kW: PRODUCTION; kWh: PAINT; kWh: OVEN; MMBTU: IR; MMBTU: 968 | 3
[31 empty] | kW: PRODUCTION; kWh: PAINT; kWh: PANEL; MMBTU: ROBOT; MMBTU: 294 | 6
[31 empty] | kW: VEHICLE; kWh: CHARGING; kWh: FORKLIFT, etc.; MMBTU: ELECTRIC; MMBTU: 10138 | 2
[31 empty] | MMBTU: TOTALS; MMBTU: 180017 | 510
[31 empty] | MMBTU: -31858.5062 | 0
[31 empty] | MMBTU: CHECKS | CHECKS
Note on AE9: Author: Default of 365 days times 24 hours per day
Note on AG9: Author: Changing plant OF only changes HOURS, not kW.
Note on AH9: Author: Changing LF will change the calculated kW.
Note on AI9: Author: Changing LF will change the calculated kW.
Note on D10: Author: Pull down menu.
Note on E10: Author: Name or Number
Note on K10: Author: This is the item actually consuming the electricity
Note on Q10: Author: Must put in a ZERO for non-motor loads.
Note on R10: Author: Use nameplate data, if available. Use EPAct Motor Efficiencies, if unknown. Table of EPAct shown on tab 3C1.
Note on S10: Author: RLA - "Running Load Amps" - current drawn during normal operation of electric motor, typically measured in plant operations and is typically lower than FLA.
Note on T10: Michael Stowe: FLA - "Full Load Amps" - amount of current drawn when full-load torque and horsepower is reached for the motor, typically determined in a lab environment. Typically higher than RLA.
Note on W10: Author: For NON Motors. Panel breaker or feeder amps from nameplate or label plate on a particular circuit or control panel.
Note on AF10: Author: Typically, if you have a diversity factor < 100% you will NOT also derate load factor. Only one or the other of DF or LF should be derated. Changing DF will change calculated kW
Note on AG10: Author: This defaults to the value in cell AA7. Enter manually if different.
Note on AH10: Author: Only one or the other of DF or LF should be derated.
Note on AI10: Author: Only one or the other of DF or LF should be derated.
Note on AT512: Author: Quantity of 8-hour per charge units
Note on AU512: Author: kW/Charger
Note on AT513: Author: Quantity of 3-hour per charge units
Note on AU513: Author: kW/Charger
Note on AN514: Author: All lighting electrical consumption values from the "Lighting Upgrade Details" tab

## 3C1_EPAct Motor Eff.
3C1 |  | Nominal Full Load Efficiencies - EPACT Electric Motors | [9 empty] | Reference Info
|  |  | Open Frame |  |  |  | Closed Frame
|  | HP | 2 Pole | 4 Pole | 6 Pole | 8 Pole | 900 | 1200 | 1800 | 3600 | RPM
[7 empty] | R | S | T | U
| 1 | 1 | N/A | 82.5 | 80 | 74 | 74 | 80 | 82.5 | 75.5
| 2 | 1.5 | 82.5 | 84 | 84 | 75.5 | 77 | 85.5 | 84 | 82.5 |  | If you do not have a motor efficiency, use this table for the motor efficiency values for column "Q" on tab 3C.
| 3 | 2 | 84 | 84 | 85.5 | 85.5 | 82.5 | 86.5 | 84 | 84
| 4 | 3 | 84 | 86.5 | 86.5 | 86.5 | 84 | 87.5 | 87.5 | 85.5
| 5 | 5 | 85.5 | 87.5 | 87.5 | 87.5 | 85.5 | 87.5 | 87.5 | 87.5
| 6 | 7.5 | 87.5 | 88.5 | 88.5 | 88.5 | 85.5 | 89.5 | 89.5 | 88.5
| 7 | 10 | 88.5 | 89.5 | 90.2 | 89.5 | 88.5 | 89.5 | 89.5 | 89.5
| 8 | 15 | 89.5 | 91 | 90.2 | 89.5 | 88.5 | 90.2 | 91 | 90.2
| 9 | 20 | 90.2 | 91 | 91 | 90.2 | 89.5 | 90.2 | 91 | 90.2
| 10 | 25 | 91 | 91.7 | 91.7 | 90.2 | 89.5 | 91.7 | 92.4 | 91
| 11 | 30 | 91 | 92.4 | 92.4 | 91 | 91 | 91.7 | 92.4 | 91
| 12 | 40 | 91.7 | 93 | 93 | 91 | 91 | 93 | 93 | 91.7
| 13 | 50 | 92.4 | 93 | 93 | 91.7 | 91.7 | 93 | 93 | 92.4
| 14 | 60 | 93 | 93.6 | 93.6 | 92.4 | 91.7 | 93.6 | 93.6 | 93
| 15 | 75 | 93 | 94.1 | 93.6 | 93.6 | 93 | 93.6 | 94.1 | 93 |  |  | 7358.4
| 16 | 100 | 93 | 94.1 | 94.1 | 93.6 | 93 | 94.1 | 94.5 | 93.6 |  |  | 0.26503
| 17 | 125 | 93.6 | 94.5 | 94.1 | 93.6 | 93.6 | 94.1 | 94.5 | 94.5
| 18 | 150 | 93.6 | 95 | 94.5 | 93.6 | 93.6 | 95 | 95 | 94.5
| 19 | 200 | 94.5 | 95 | 94.5 | 93.6 | 94.1 | 95 | 95 | 95
| 20 | 250 | 94.5 | 95.4 | 95.4 | 94.5 | 94.5 | 95 | 95 | 95.4
| 21 | 300 | 95 | 95.4 | 95.4 | N/A | N/A | 95 | 95.4 | 95.4
| 22 | 350 | 95 | 95.4 | 95.4 | N/A | N/A | 95 | 95.4 | 95.4
| 23 | 400 | 95.4 | 95.4 | N/A | N/A | N/A | N/A | 95.4 | 95.4
| 24 | 450 | 95.8 | 95.8 | N/A | N/A | N/A | N/A | 95.4 | 95.4
| 25 | 500 | 95.8 | 95.8 | N/A | N/A | N/A | N/A | 95.8 | 95.4
TYPICAL

## 3D_Combustion Equip Master
3D |  |  | ANY SITE | [5 empty] | COLUMN COLOR KEY |  |  |  |  | COLUMN COLOR KEY | [5 empty] | I = Intermittent, on and off, as needed, but not a continuous load, when ON, runs at full load | [11 empty] | COLUMN COLOR KEY
|  |  |  | Combustion Equipment Master |  |  |  |  | DATA YOU CAN GET |  |  |  |  | DATA YOU CAN GET |  |  |  | Percent Factor |  | L = ON and runs continuously during operations of associated manufacturing line | [11 empty] | DATA YOU CAN GET
[7 empty] | ALL Natural Gas on ONE |  | DECISION NEEDED, then INPUT Values |  |  |  |  | DECISION NEEDED, then INPUT Values |  |  | Winter Hours | 50% |  | V = Variable loads, equipment is ON, but ramps up and down depending on plant needs (air compressors & chillers) | [11 empty] | DECISION NEEDED, then INPUT Values
[7 empty] | Other Combustion MMBTU from this table: | 7962 | CALCULATED with FORMULA |  |  |  |  | CALCULATED with FORMULA |  |  | Summer Hours | 50% |  | B = ON all the time (i.e. base load, servers, lighting, offices, certain fans, safety equipment, etc.) | [11 empty] | CALCULATED with FORMULA
[7 empty] | Total Estimated ANNUAL Natural Gas MMBTU from this table: | 275251.1278 | MMBTU | [10 empty] | DF = Diversity Factor, to account for things like oven heating, hot water heating, etc. (fossil fuel heating)
[7 empty] | Total actual ANNUAL MMBTU from all natural gas invoices: | 279739.5055 | MMBTU | [7 empty] | Full Year | Plant Hours | OF | LF = Load factor for the item, when running/operating. If the items runs at full load during operations, then the LF is 100%
[5 empty] | For the year: |  | 2022 | [8 empty] | PLANT Operational Factor: | 8760 | 5400 | 61.64% | OF = Operational Factor for the plant. What percentage of the total time is the plant running. | [15 empty] | February | August
[7 empty] | DELTA: | -4488.3778 | -1.604% | [10 empty] | SF = Seasonal Factor should be YES for loads impacted by the season and weather conditions | [15 empty] | Winter | Summer | Winter | Summer
For Sort | [5 empty] | SORT 1 | SORT 2 |  |  |  | SORT 3 | SORT 4 |  |  |  | Nameplate Data from Combustion Burner Equipment |  |  |  | OPS | SF | TOTAL HRS |  | PLANT | Winter | Summer | Winter | Summer | Winter | Summer |  | Sub-Metering Info: Measured |  |  |  | Measured | Measured | Calculated | Calculated
#1 | #2 | #3 | SITE | BUILDING | DEPT. | GROUP | SYSTEM | AREA | LOCATION | EQUIPMENT | EQUIPMENT 1 | EQUIPMENT 2 | ASSET # | DESCRIPTION | QUANTITY | BTU/HR | COMBEFF | Other | Other | CODE | Y/N | FULL YEAR | DF | OF | LF | LF | ∑HRS | ∑HRS | MMBTU | MMBTU | Any Additional Comments | Metered | Recorded By | Verification | Calibration | MMBTU | MMBTU | MMBTU | MMBTU
1 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line A) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1195200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2420.28 | 2420.28 | [7 empty] | 2420.28 | 2420.28
2 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #1 | Combustion Burner #1 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 702000 | 80% |  |  | L | YES | 8760 | 60% | 61.64% | 100% | 0% | 2700 | 2700 | 1421.55 | 0 | [7 empty] | 1421.55 | 0
3 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #1 | Combustion Burner #2 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 702000 | 80% |  |  | L | YES | 8760 | 60% | 61.64% | 100% | 0% | 2700 | 2700 | 1421.55 | 0 | [7 empty] | 1421.55 | 0
4 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #1 | Combustion Burner #3 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 702000 | 80% |  |  | L | YES | 8760 | 60% | 61.64% | 100% | 0% | 2700 | 2700 | 1421.55 | 0 | [7 empty] | 1421.55 | 0
5 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #1 | Combustion Burner #4 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 702000 | 80% |  |  | L | YES | 8760 | 60% | 61.64% | 100% | 0% | 2700 | 2700 | 1421.55 | 0 | [7 empty] | 1421.55 | 0
6 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Heater Box (Line A) | Combustion Burner #1 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 398400 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 806.76 | 806.76 | [7 empty] | 806.76 | 806.76
7 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Heater Box (Line A) | Combustion Burner #2 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 398400 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 806.76 | 806.76 | [7 empty] | 806.76 | 806.76
8 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Heater Box (Line A) | Combustion Burner #3 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 398400 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 806.76 | 806.76 | [7 empty] | 806.76 | 806.76
9 | [5 empty] | PRODUCTION | PAINT | Chassis Dry-Off Booth | Dry-Off Booth (Line B) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1195200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2420.28 | 2420.28 | [7 empty] | 2420.28 | 2420.28
10 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #2 | Combustion Burner #1 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1404000 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2843.1 | 2843.1 | [7 empty] | 2843.1 | 2843.1
11 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out | Heater Box ASH #2 | Combustion Burner #2 | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1404000 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2843.1 | 2843.1 | [7 empty] | 2843.1 | 2843.1
12 | [5 empty] | PRODUCTION | PAINT | Chassis Black-Out Oven | Heater Box (Line B) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1195200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2420.28 | 2420.28 | [7 empty] | 2420.28 | 2420.28
13 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 1 | Booth No. 1 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1123200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2274.48 | 2274.48 | [7 empty] | 2274.48 | 2274.48
14 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 2 | Booth No. 2 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1123200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2274.48 | 2274.48 | [7 empty] | 2274.48 | 2274.48
15 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 3 | Booth No. 3 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1123200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2274.48 | 2274.48 | [7 empty] | 2274.48 | 2274.48
16 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 4 | Booth No. 4 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1123200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2274.48 | 2274.48 | [7 empty] | 2274.48 | 2274.48
17 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 5 | Booth No. 5 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1123200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2274.48 | 2274.48 | [7 empty] | 2274.48 | 2274.48
18 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 6 | Booth No. 6 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1123200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2274.48 | 2274.48 | [7 empty] | 2274.48 | 2274.48
19 | [5 empty] | PRODUCTION | PAINT | Reprocess Booth No. 7 | Booth No. 7 Small Parts | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 561600 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1137.24 | 1137.24 | [7 empty] | 1137.24 | 1137.24
20 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Tank Water Heating | Combustion Burner | WASHER | COMB |  | Combustion burner, fueled by natural gas | 1 | 243000 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 492.075 | 492.075 | [7 empty] | 492.075 | 492.075
21 | [5 empty] | PRODUCTION | PAINT | Hood Paint Washer | Tank Water Heating | Combustion Burner | WASHER | COMB |  | Combustion burner, fueled by natural gas | 1 | 243000 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 492.075 | 492.075 | [7 empty] | 492.075 | 492.075
22 | [5 empty] | PRODUCTION | PAINT | Hood Dry-Off Oven | Dry-Off Oven (D126LOS) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 111276 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 225.3339 | 225.3339 | [7 empty] | 225.3339 | 225.3339
23 | [5 empty] | PRODUCTION | PAINT | Hood Spray Booth | Base Coat ASH | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1010880 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 2047.032 | 2047.032 | [7 empty] | 2047.032 | 2047.032
24 | [5 empty] | PRODUCTION | PAINT | Hood Clear Coat | Clear Coat Air House | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 673920 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1364.688 | 1364.688 | [7 empty] | 1364.688 | 1364.688
25 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Hood Oven Heater Box Zone #1 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 111276 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 225.3339 | 225.3339 | [7 empty] | 225.3339 | 225.3339
26 | [5 empty] | PRODUCTION | PAINT | Hood Paint Oven | Hood Oven Heater Box Zone #2 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 20232 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 40.9698 | 40.9698 | [7 empty] | 40.9698 | 40.9698
27 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Burner | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 702000 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1421.55 | 1421.55 | [7 empty] | 1421.55 | 1421.55
28 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #2 | Booth #2 Burner | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 702000 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1421.55 | 1421.55 | [7 empty] | 1421.55 | 1421.55
29 | [5 empty] | PRODUCTION | PAINT | Hood Paint Booth #1 | Booth #1 Oven Heater Box | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 45500 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 92.1375 | 92.1375 | [7 empty] | 92.1375 | 92.1375
30 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth North AHU Burner | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 561600 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1137.24 | 1137.24 | [7 empty] | 1137.24 | 1137.24
31 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Booth South AHU Burner | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 561600 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1137.24 | 1137.24 | [7 empty] | 1137.24 | 1137.24
32 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Radiant Zone | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 22750 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 46.0688 | 46.0688 | [7 empty] | 46.0688 | 46.0688
33 | [5 empty] | PRODUCTION | PAINT | Hood Paint Tennessee | Tennessee Oven - Turbulent Zone | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 22750 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 46.0688 | 46.0688 | [7 empty] | 46.0688 | 46.0688
34 | [5 empty] | FACILITY | HOT WATER | Pretreatment | Hot Water Boiler Heater | Combustion Burner | HEATING | COMB |  | Combustion burner, fueled by natural gas | 1 | 316564 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 641.0421 | 641.0421 | [7 empty] | 641.0421 | 641.0421
35 | [5 empty] | PRODUCTION | PAINT | Pretreat Oven | Pretreat Oven Heater Box | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 491220 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 994.7205 | 994.7205 | [7 empty] | 994.7205 | 994.7205
36 | [5 empty] | PRODUCTION | PAINT | Supply Primer Booth | ASH #5B | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 1881360 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 3809.754 | 3809.754 | [7 empty] | 3809.754 | 3809.754
37 | [5 empty] | PRODUCTION | PAINT | Primer Oven | Oven Heater Box (Combustion) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 491220 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 994.7205 | 994.7205 | [7 empty] | 994.7205 | 994.7205
38 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 772200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1563.705 | 1563.705 | [7 empty] | 1563.705 | 1563.705
39 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 772200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1563.705 | 1563.705 | [7 empty] | 1563.705 | 1563.705
40 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Tack-Off | ASH #3 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 772200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1563.705 | 1563.705 | [7 empty] | 1563.705 | 1563.705
41 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 772200 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1563.705 | 1563.705 | [7 empty] | 1563.705 | 1563.705
42 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Tack-Off | ASH #3 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 393120 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 796.068 | 796.068 | [7 empty] | 796.068 | 796.068
43 | [5 empty] | PRODUCTION | PAINT | Booth #3 Cut-In | ASH #9 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 393120 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 796.068 | 796.068 | [7 empty] | 796.068 | 796.068
44 | [5 empty] | PRODUCTION | PAINT | Booth #3 Cut-In | ASH #9 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 393120 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 796.068 | 796.068 | [7 empty] | 796.068 | 796.068
45 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 393120 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 796.068 | 796.068 | [7 empty] | 796.068 | 796.068
46 | [5 empty] | PRODUCTION | PAINT | #1, #2, & #3 Booth | ASH #1 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 393120 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 796.068 | 796.068 | [7 empty] | 796.068 | 796.068
47 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 542880 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1099.332 | 1099.332 | [7 empty] | 1099.332 | 1099.332
48 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 542880 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1099.332 | 1099.332 | [7 empty] | 1099.332 | 1099.332
49 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 542880 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1099.332 | 1099.332 | [7 empty] | 1099.332 | 1099.332
50 | [5 empty] | PRODUCTION | PAINT | #4 & #5 Tack-Off | ASH #4 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 542880 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1099.332 | 1099.332 | [7 empty] | 1099.332 | 1099.332
51 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 542880 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1099.332 | 1099.332 | [7 empty] | 1099.332 | 1099.332
52 | [5 empty] | PRODUCTION | PAINT | Booth 4/5 & Flash-Off | ASH #2 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 542880 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1099.332 | 1099.332 | [7 empty] | 1099.332 | 1099.332
53 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1 (Radiant) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 491220 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 994.7205 | 994.7205 | [7 empty] | 994.7205 | 994.7205
54 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #1(Convection) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 136450 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 276.3112 | 276.3112 | [7 empty] | 276.3112 | 276.3112
55 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Radiant) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 491220 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 994.7205 | 994.7205 | [7 empty] | 994.7205 | 994.7205
56 | [5 empty] | PRODUCTION | PAINT | Top Coat Oven | Top Coat Oven #2 (Convection) | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 136450 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 276.3112 | 276.3112 | [7 empty] | 276.3112 | 276.3112
57 | [5 empty] | PRODUCTION | PAINT | Booth #6 | ASH #6 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 486720 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 985.608 | 985.608 | [7 empty] | 985.608 | 985.608
58 | [5 empty] | PRODUCTION | PAINT | Booth #6 | ASH #6 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 486720 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 985.608 | 985.608 | [7 empty] | 985.608 | 985.608
59 | [5 empty] | PRODUCTION | PAINT | #6 Tack & Flash-Off | ASH #7 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 486720 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 985.608 | 985.608 | [7 empty] | 985.608 | 985.608
60 | [5 empty] | PRODUCTION | PAINT | Booth #7 & Tack-Off | ASH #8 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 730080 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1478.412 | 1478.412 | [7 empty] | 1478.412 | 1478.412
61 | [5 empty] | PRODUCTION | PAINT | Booth #7 & Tack-Off | ASH #8 | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 730080 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 1478.412 | 1478.412 | [7 empty] | 1478.412 | 1478.412
62 | [5 empty] | PRODUCTION | PAINT | Multi Color Oven | Multi Color Oven | Combustion Burner | OVEN | COMB |  | Combustion burner, fueled by natural gas | 1 | 145120 | 80% |  |  | L | NO | 8760 | 60% | 61.64% | 100% | 100% | 2700 | 2700 | 293.868 | 293.868 | [7 empty] | 293.868 | 293.868
63 | [5 empty] | FACILITY | HVAC | Offline |  | Radiant Heater-1 | HEATING | COMB |  | Space Ray RSCA6-N1 Radiant Heater, natural gas | 1 | 52000 | 48% |  |  | I | YES | 8760 | 100% | 100% | 100% | 0% | 4380 | 4380 | 474.5 | 0 | [7 empty] | 474.5 | 0
64 | [5 empty] | FACILITY | HVAC |  |  | Radiant Heater-2 | HEATING | COMB |  | Space Ray RCSA3-N5 Radiant Heater, natural gas | 1 | 26000 | 48% |  |  | I | YES | 8760 | 100% | 100% | 100% | 0% | 4380 | 4380 | 237.25 | 0 | [7 empty] | 237.25 | 0
65 | [5 empty] | FACILITY | HVAC |  |  | UH-2 - UH-5 | HEATING | COMB |  | Trane GPND-010ADD1000, Unit Heater | 4 | 100000 | 80% |  |  | I | YES | 8760 | 100% | 100% | 100% | 0% | 4380 | 4380 | 2190 | 0 | [7 empty] | 2190 | 0
66 | [5 empty] | FACILITY | BOILER | Office | Office | Boiler No.1 | COMFORT | COMB |  | Office Boiler, Natural Gas-fired (1.02 million BTU per hour maximum heat input). | 1 | 1020000 | 83% |  |  | V | YES | 8760 | 100% | 60% | 100% | 0% | 2628 | 2628 | 3229.5904 | 0 | [7 empty] | 3229.5904 | 0
67 | [5 empty] | FACILITY | BOILER |  | Boiler Room | Boiler No.3 | BOILER | COMB |  | Boiler Room 400A, Natural gas-fired (8.37 million BTU per hour maximum heat input). | 1 | 8370000 | 80% |  |  | V | YES | 8760 | 100% | 60% | 100% | 50% | 2628 | 2628 | 27495.45 | 13747.725 | [7 empty] | 27495.45 | 13747.725
68 | [5 empty] | FACILITY | BOILER |  | Hood Paint Center | Boiler No.4 | BOILER | COMB |  | Hood paint center, natural gas-fired (5.14 million BTU per hour maximum heat input) | 1 | 5140000 | 80% |  |  | V | YES | 8760 | 100% | 60% | 100% | 50% | 2628 | 2628 | 16884.9 | 8442.45 | [7 empty] | 16884.9 | 8442.45
69 | [5 empty] | FACILITY | BOILER |  | Mechanical Room | Boiler No.5 | BOILER | COMB |  | Main Boiler, Mechanical Room natural gas-fired (33.6 million BTU per hour maximum heat input). | 1 | 33600000 | 75% |  |  | V | YES | 8760 | 100% | 40% | 60% | 0% | 1752 | 1752 | 47093.76 | 0 | [7 empty] | 47093.76 | 0
70 | [5 empty] | FACILITY | HVAC | Offline | Offline | Unit Heaters | HEATING | COMB |  | Overhead mounted unit heaters-gas fired | 32 | 80000 | 80% |  |  | I | YES | 8760 | 60% | 60% | 100% | 0% | 2628 | 2628 | 5045.76 | 0
71 | [5 empty] | VEHICLE | LP-IC | Plant Wide | Plant Wide | Lifts and Utility Vehicles | FORKLIFT, etc. | LP-IC |  | Vehicle powered by Liquid Propane (LP) | 85 |  |  |  |  | I | NO | 8760 | 100% | 61.64% | 100% | 100% |  |  | 3884.5 | 3884.5 | [7 empty] | 3884.5 | 3884.5
72 | [5 empty] | VEHICLE | DIESEL | Plant Wide-Yard | Plant Wide-Yard | Lifts and Utility Vehicles | FORKLIFT, etc. | DIESEL |  | Vehicle powered by Diesel Fuel | 5 |  |  |  |  | I | NO | 8760 | 100% | 61.64% | 100% | 100% |  |  | 96.5 | 96.5 | [7 empty] | 96.5 | 96.5
73 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
74 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
75 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
76 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
77 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
78 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
79 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
80 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
81 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
82 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
83 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
84 | [21 empty] | 8760 |  | 61.64% | 100% | 100%
| INSERT LINES ONLY - DO NOT DRAG DOWN | [18 empty] | INFO Only | INFO Only |  | Changes MMBTU | Changes Hours | Changes MMBTU | Changes MMBTU |  | N.G. TOTALS | 180699.1816 | 94551.9462 | 275251.1278 | [6 empty] | 179634.4216 | 98532.9462
[29 empty] | Winter | Summer | [8 empty] | 278167.3678
[29 empty] | MMBTU | MMBTU
[28 empty] | Vehicle | LP | LP
[28 empty] | Fork Lifts | 3884.5 | 3884.5 | 7769 | 283213.1278
[9 empty] | SEASONAL Effected Load | [19 empty] | 2.15% | 4.108%
|  |  | Site Pull Down |  | OPS CODE Pull DOWN |  |  |  | Sub-Metered Load | [18 empty] | Vehicle | DIESEL | DIESEL
[9 empty] | YES | [18 empty] | Fork Lifts | 96.5 | 96.5 | 193
[5 empty] | B |  |  |  | NO | [19 empty] | 0.0534% | 0.1021%
I
[5 empty] | L | [22 empty] | The tables below are created manually by sorting the above lines.
[5 empty] | V | [22 empty] | These do not update automatically.
The data from the tables below are used to create Energy USE pie charts.
[26 empty] | GROUP | SYSTEM | EQUIPMENT 1 | EQUIPMENT 2
[26 empty] | SORT 1 | SORT 2 | SORT 3 | SORT 4 | MMBTU | # of Line Items
[26 empty] | FACILITY | BOILER | HEATING | COMFORT | 9351.52 | 4 | 0.08
[26 empty] | FACILITY | BOILER | HEATING | PROCESS | 107542.48 | 0 | 0.92
[26 empty] | FACILITY | HOT WATER | HEATING | COMB | 1282 | 1
[26 empty] | PRODUCTION | PAINT | OVEN | COMB | 152846 | 59
[26 empty] | FACILITY | HVAC | HEATING | COMB | 7948 | 4
[26 empty] | VEHICLE | LP-IC | FORKLIFT, etc. | LP-IC | 7769 | 1
[26 empty] | VEHICLE | DIESEL | FORKLIFT, etc. | DIESEL | 193 | 1
[26 empty] | PRODUCTION | PAINT | WASHER | COMB | 1968 | 2
[29 empty] | TOTALS | 288900 | 72
283213.1278
-5686.8722
CHECKS
[28 empty] | KEY 1 | KEY 2
[28 empty] | SORT 1 | SORT 2 | MMBTU | # of Line Items
[28 empty] | BOILER | COMB | 118296 | 4
[28 empty] | HEAT | COMB | 2190 | 1
[28 empty] | HEAT | RADI | 712 | 2
[28 empty] | HW HTR | COMB | 1088 | 1
[28 empty] | OVEN | COMB | 129730 | 59
[28 empty] | VEHICLE | LP | 7769 | 1
[28 empty] | VEHICLE | DIESEL | 193 | 1
[28 empty] | WASH | COMB | 1671 | 2
[29 empty] | TOTALS | 261649 | 71
Note on W9: Author: Default of 365 days times 24 hours per day
Note on AK9: Author: Convert from meter units to MMBTU, as needed
Note on AL9: Author: Convert from meter units to MMBTU, as needed
Note on D10: Author: Pull down menu.
Note on E10: Author: Name or Number
Note on K10: Author: This is the item actually consuming the electricity
Note on R10: Author: Estimated combustion efficiency. Or actual data, if known.
Note on X10: Author: Typically, if you have a diversity factor < 100% you will NOT also derate load factor. Only one or the other of DF or LF should be derated.
Note on Y10: Author: This defaults to the value in cell S7. Enter manually if different.
Note on Z10: Author: Only one or the other of DF or LF should be derated.
Note on AA10: Author: Only one or the other of DF or LF should be derated.

## 3E_Diversity Factor
3E
Diversity Factor Examples
Reference Info
The two examples below demonstrate the diversity factor and how to estimate this.
|  | Electric | [5 empty] | Natural Gas
| 1,000 kwh Electric Oven | [5 empty] | 1,000,000 BTU/HR Natural Gas Oven
| Operational Temperature: 450 ºF | [5 empty] | Operational Temperature: 450 ºF
|  |  | Oven |  |  |  |  | BTU/HR | Oven
| Hour | kW | Temp |  |  |  | Hour | Rate | Temp
| 0 | 0 | 80 |  | Total kWh |  | 0 | 0 | 80 | Total BTU
| 1 | 1000 | 400 |  | 5500 |  | 1 | 1000000 | 160 | 6000000
| 2 | 700 | 450 |  | 750 |  | 2 | 1000000 | 240 | 4500000
| 3 | 500 | 448 |  | 6250 |  | 3 | 1000000 | 320 | 10500000
| 4 | 450 | 452 |  |  |  | 4 | 1000000 | 420
| 5 | 500 | 448 |  | 520.8333 | Average kW | 5 | 750000 | 450 | 656250 | Average BTU/hour
| 6 | 450 | 452 |  | 52.08% |  | 6 | 450000 | 445 | 65.62%
| 7 | 500 | 448 |  | D.F. |  | 7 | 500000 | 455 | D.F.
| 8 | 450 | 452 |  |  |  | 8 | 450000 | 445
| 9 | 500 | 448 |  |  |  | 9 | 500000 | 455
| 10 | 450 | 452 |  |  |  | 10 | 450000 | 445
| 11 | 500 | 448 |  |  |  | 11 | 500000 | 455
| 12 | 0 | 80 |  |  |  | 12 | 450000 | 445
[7 empty] | 13 | 500000 | 455
[7 empty] | 14 | 400000 | 445
[7 empty] | 15 | 0 | 300
[7 empty] | 16 | 0 | 150

## 4_Utility Data
4 | ANY SITE
Energy Mapping Process for ANY SITE
Utility Data and Relevant Variables
Cut and Paste, or link this tab to your EnPI model "Input Raw Data" Tab
All plants have EnPI models with this information already collected.
Site Input Raw Data table from the EnPI Model
|  |  | Energy Input Data |  |  |  | Possible Relevant Variables
|  |  |  | PRIMARY (*3) |  |  | PRODUCTION | PRODUCTION | PRODUCTION |  |  |  | TOTAL ENERGY
|  | Actual Date * | Electricity (kWh site) | Electricity (MMBTU) | Natural Gas (kWh) | Natural Gas (MMBTU) | UNITS | Manhours | Paint (Gallons) | Heating Degree Days (HDD) | Cooling Degree Days (CDD) | Period | MMBTU (Site)
|  | 2013-01-01 | 4164952 | 42634.2229 | 8349246.6 | 28488.815 | 1777 | 236078 | 31775 | 771 | 0 | 2013-01-01 | 42700.2226
|  | 2013-02-01 | 3504019 | 35868.6312 | 9502008.9 | 32422.2037 | 1984.4 | 223078 | 31500 | 749 | 0 | 2013-02-01 | 44378.4141
|  | 2013-03-01 | 4297455 | 43990.5801 | 5112543.3 | 17444.7237 | 1895.3 | 244159 | 37438 | 755 | 0 | 2013-03-01 | 32108.2504
|  | 2013-04-01 | 4530771 | 46378.9021 | 4196019.6 | 14317.4147 | 1899.2 | 240143 | 33682 | 281 | 13 | 2013-04-01 | 29777.0487
|  | 2013-05-01 | 5562059 | 56935.6054 | 3189221.1 | 10882.0753 | 1704.7 | 229577 | 33735 | 130 | 52 | 2013-05-01 | 29860.6104
|  | 2013-06-01 | 5781759 | 59184.5482 | 3073739.7 | 10488.0363 | 1868.1 | 201840 | 33251 | 0 | 226 | 2013-06-01 | 30216.219
|  | 2013-07-01 | 6006005 | 61480.0257 | 3265427.1 | 11142.101 | 1866.1 | 224768 | 35160 | 0 | 319 | 2013-07-01 | 31635.4429
|  | 2013-08-01 | 5728576 | 58640.1443 | 3666094.8 | 12509.236 | 1751.1 | 230084 | 34522 | 6 | 239 | 2013-08-01 | 32055.9508
|  | 2013-09-01 | 4810119 | 49238.4272 | 6147479.4 | 20976.0727 | 2020.3 | 215844 | 31045 | 36 | 117 | 2013-09-01 | 37388.8817
|  | 2013-10-01 | 4724452 | 48361.5033 | 8731742.1 | 29793.944 | 1532.7 | 254262 | 38981 | 233 | 17 | 2013-10-01 | 45914.445
|  | 2013-11-01 | 4397447 | 45014.1408 | 8454469.5 | 28847.8505 | 1375.3 | 209969 | 26646 | 643 | 0 | 2013-11-01 | 43852.5641
|  | 2013-12-01 | 4397447 | 45014.1408 | 16407738 | 55985.532 | 1375.3 | 197644 | 22581 | 719 | 0 | 2013-12-01 | 70990.2456
|  | 2014-01-01 | 3517235 | 36003.9158 | 12403112 | 42321.1794 | 1914 | 259853 | 29751 | 1068 | 0 | 2014-01-01 | 54322.4847
|  | 2014-02-01 | 4423642 | 45282.284 | 10798097 | 36844.6403 | 1722 | 229340 | 29053 | 693 | 0 | 2014-02-01 | 51938.735
|  | 2014-03-01 | 7031119 | 71973.5293 | 7497204 | 25581.5247 | 2114 | 280684 | 28107 | 711 | 0 | 2014-03-01 | 49572.7011
|  | 2014-04-01 | 4821998 | 49360.0257 | 4694110 | 16016.9699 | 2086 | 282183 | 39300 | 284 | 4 | 2014-04-01 | 32470.3118
|  | 2014-05-01 | 5268644 | 53932.0844 | 3587166 | 12239.9198 | 2186 | 309967 | 32192 | 70 | 102 | 2014-05-01 | 30217.2812
|  | 2014-06-01 | 5906435 | 60460.7848 | 3549109 | 12110.0639 | 2193 | 334395 | 35936 | 2 | 262 | 2014-06-01 | 32263.6588
|  | 2014-07-01 | 6056663 | 61998.5826 | 3288289 | 11220.109 | 2621 | 373362 | 41918 | 0 | 286 | 2014-07-01 | 31886.3032
|  | 2014-08-01 | 6548698 | 67035.2625 | 2739257 | 9346.7339 | 2479 | 373221 | 37965 | 1 | 217 | 2014-08-01 | 31691.8213
|  | 2014-09-01 | 6105600 | 62499.5226 | 2740191 | 9349.9208 | 2454 | 390379 | 44944 | 31 | 149 | 2014-09-01 | 30183.095
|  | 2014-10-01 | 5024764 | 51435.6249 | 5798470 | 19785.203 | 2700 | 444263 | 43307 | 223 | 16 | 2014-10-01 | 36930.4113
|  | 2014-11-01 | 4887568 | 50031.2282 | 9385648 | 32025.1637 | 2048 | 363429 | 25351 | 688 | 0 | 2014-11-01 | 48702.2398
|  | 2014-12-01 | 4537911 | 46451.9901 | 9137672 | 31179.0344 | 2048 | 381236 | 40389 | 729 | 0 | 2014-12-01 | 46663.0311
|  | 2015-01-01 | 4022006 | 41170.9668 | 15237758 | 51993.3941 | 2644 | 455114 | 46803 | 922 | 0 | 2015-01-01 | 65717.0497
|  | 2015-02-01 | 4967702 | 50851.5139 | 15353200 | 52387.2986 | 2790 | 421595 | 45522 | 922 | 0 | 2015-02-01 | 69337.8032
|  | 2015-03-01 | 4621016 | 47302.6883 | 9653471 | 32939.0138 | 2707 | 459390 | 54317 | 543 | 0 | 2015-03-01 | 48706.5766
|  | 2015-04-01 | 4864901 | 49799.1991 | 5680684 | 19383.3005 | 3019 | 438370 | 49067 | 274 | 22 | 2015-04-01 | 35983.0335
|  | 2015-05-01 | 5446778 | 55755.5399 | 3733699 | 12739.9112 | 2946 | 414955 | 49704 | 47 | 116 | 2015-05-01 | 31325.0912
|  | 2015-06-01 | 6179017 | 63251.0503 | 2714938 | 9263.754 | 3173 | 459956 | 51465 | 6 | 326 | 2015-06-01 | 30347.4374
|  | 2015-07-01 | 6642565 | 67996.1251 | 2443034 | 8335.9789 | 2988 | 453940 | 62149 | 0 | 378 | 2015-07-01 | 31001.3539
|  | 2015-08-01 | 7073003 | 72402.2718 | 2307375 | 7873.0911 | 2918 | 446655 | 48412 | 0 | 298 | 2015-08-01 | 32007.1817
|  | 2015-09-01 | 6234949 | 63823.5941 | 3849727 | 13135.8152 | 3001 | 461365 | 50352 | 34 | 138 | 2015-09-01 | 34410.3465
|  | 2015-10-01 | 5603891 | 57363.8155 | 7691543 | 26244.6369 | 3153 | 484882 | 54325 | 256 | 6 | 2015-10-01 | 45365.9088
|  | 2015-11-01 | 5039779 | 51589.3248 | 6625023 | 22605.5192 | 1794 | 331986 | 32033 | 446 | 1 | 2015-11-01 | 39801.9608
|  | 2015-12-01 | 4243891 | 43442.2762 | 6936775 | 23669.2613 | 2027 | 307323 | 38331 | 475 | 5 | 2015-12-01 | 38150.02
|  | 2016-01-01 | 3514215 | 35973.0018 | 13921016 | 47500.4834 | 1794 | 165319 | 34717 | 956 | 0 | 2016-01-01 | 59491.484
|  | 2016-02-01 | 4406172 | 45103.4536 | 11452784 | 39078.5253 | 1743 | 179610 | 29160 | 752 | 0 | 2016-02-01 | 54113.0098
|  | 2016-03-01 | 3869150 | 39606.2677 | 6147140 | 20974.9146 | 1644 | 216247 | 36186 | 398 | 2 | 2016-03-01 | 34177.0038
|  | 2016-04-01 | 4236179 | 43363.3329 | 5123984 | 17483.761 | 1569 | 204889 | 37145 | 287 | 28 | 2016-04-01 | 31938.2053
|  | 2016-05-01 | 4400509 | 45045.4847 | 3893970 | 13286.7786 | 1585 | 201131 | 30637 | 107 | 61 | 2016-05-01 | 28301.9402
|  | 2016-06-01 | 5072456 | 51923.8205 | 2722263 | 9288.7479 | 1651 | 207360 | 39214 | 0 | 270 | 2016-06-01 | 26596.6881
|  | 2016-07-01 | 5533482 | 56643.079 | 2723435 | 9292.7469 | 1434 | 175627 | 29911 | 0 | 429 | 2016-07-01 | 28173.7733
|  | 2016-08-01 | 5302696 | 54280.6552 | 2118097 | 7227.2477 | 1730 | 213943 | 33443 | 0 | 390 | 2016-08-01 | 25320.7995
|  | 2016-09-01 | 4960000 | 50772.673 | 1682992 | 5742.6077 | 1589 | 201077 | 33479 | 0 | 243 | 2016-09-01 | 22666.832
|  | 2016-10-01 | 4618775 | 47279.7485 | 4162065 | 14201.5568 | 1575 | 194768 | 34178 | 166 | 15 | 2016-10-01 | 29961.473
|  | 2016-11-01 | 3942547 | 40357.5906 | 5717309 | 19508.2702 | 1405 | 171709 | 29321 | 479 | 0 | 2016-11-01 | 32960.8004
|  | 2016-12-01 | 3748018 | 38366.3089 | 9194633 | 31373.3934 | 1221 | 153344 | 31679 | 767 | 0 | 2016-12-01 | 44162.1631
|  | 2017-01-01 | 3532063 | 36155.7015 | 9378637 | 32001.2412 | 1576 | 193277 | 25906 | 751 | 0 | 2017-01-01 | 44053.1417
|  | 2017-02-01 | 3841201 | 39320.1698 | 6394139 | 21817.7102 | 1504 | 183052 | 26156 | 484 | 0 | 2017-02-01 | 34924.4335
|  | 2017-03-01 | 3644224 | 37303.8293 | 7678065 | 26198.6481 | 1744 | 210301 | 31349 | 557 | 2 | 2017-03-01 | 38633.2578
|  | 2017-04-01 | 4170606 | 42692.0997 | 3848848 | 13132.8159 | 1482 | 180803 | 28483 | 160 | 50 | 2017-04-01 | 27363.5158
|  | 2017-05-01 | 4426660 | 45313.1775 | 3769445 | 12861.8816 | 1827 | 226939 | 32184 | 72 | 95 | 2017-05-01 | 27966.2741
|  | 2017-06-01 | 5320647 | 54464.4093 | 2675090 | 9127.7869 | 1878 | 236596 | 44474.0167 | 2 | 237 | 2017-06-01 | 27282.59
|  | 2017-07-01 | 5913117 | 60529.1846 | 2046312 | 6982.3071 | 1620 | 207232 | 32274 | 0 | 389 | 2017-07-01 | 27158.702
|  | 2017-08-01 | 6029935 | 61724.9834 | 2523023 | 8608.9127 | 1888 | 241509 | 34841 | 0 | 260 | 2017-08-01 | 29183.9072
|  | 2017-09-01 | 5337856 | 54640.5679 | 3130119 | 10680.4105 | 1607 | 212234 | 24618 | 41 | 121 | 2017-09-01 | 28893.9332
|  | 2017-10-01 | 4837630 | 49520.0415 | 4564940 | 15576.2235 | 1743 | 222366 | 32472 | 232 | 50 | 2017-10-01 | 32082.904 | SITE | SITE
|  | 2017-11-01 | 3941820 | 40350.1487 | 6528333 | 22275.5992 | 1503 | 196708 | 28834 | 554 | 0 | 2017-11-01 | 35725.6488 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2017-12-01 | 3524584.83 | 36079.1518 | 7429308 | 25349.8539 | 1189 | 167211 | 19896 | 787 | 0 | 2017-12-01 | 37376.2378 | 54520343.83 | 204613.3909
|  | 2018-01-01 | 3439105.67 | 35204.1507 | 12166825 | 41514.9346 | 1681 | 228005 | 28654 | 1024 | 0 | 2018-01-01 | 53249.6515
|  | 2018-02-01 | 3453525.9 | 35351.7623 | 6183472 | 21098.8845 | 1698 | 232834 | 24535 | 492 | 1 | 2018-02-01 | 32882.8053
|  | 2018-03-01 | 3912945.94 | 40054.5816 | 7914223 | 27004.4527 | 1728 | 279410 | 31346 | 651 | 1 | 2018-03-01 | 40355.9799
|  | 2018-04-01 | 4304298.05 | 44060.6285 | 4924451 | 16802.9261 | 1812 | 324422 | 38883 | 322 | 7 | 2018-04-01 | 31489.8022
|  | 2018-05-01 | 5625730.3 | 57587.3719 | 3406125 | 11622.1822 | 2394 | 363803 | 44025 | 20 | 201 | 2018-05-01 | 30817.9728
|  | 2018-06-01 | 6320328.69 | 64697.5769 | 2725486 | 9299.7453 | 1800 | 361835 | 44474 | 0 | 324 | 2018-06-01 | 30865.6042
|  | 2018-07-01 | 6811817.99 | 69728.6708 | 2279247 | 7777.1144 | 1606 | 356749 | 35692 | 0 | 370 | 2018-07-01 | 31020.0047
|  | 2018-08-01 | 6822148.75 | 69834.4208 | 3001785 | 10242.5167 | 2148 | 395020 | 43758 | 0 | 338 | 2018-08-01 | 33520.657
|  | 2018-09-01 | 6471340.71 | 66243.4003 | 2947287 | 10056.5618 | 1807 | 343189 | 37819 | 0 | 291 | 2018-09-01 | 32137.6952
|  | 2018-10-01 | 5897388.41 | 60368.1801 | 6707942 | 22888.4506 | 2767 | 431497 | 52855 | 243 | 90 | 2018-10-01 | 43011.1773 | SITE | SITE
|  | 2018-11-01 | 4659986.07 | 47701.6026 | 10385385 | 35436.4083 | 2381 | 387041 | 53565 | 621 | 0 | 2018-11-01 | 51336.9425 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2018-12-01 | 4270928.59 | 43719.0445 | 10097952 | 34455.6461 | 1590 | 313053 | 23627 | 760 | 0 | 2018-12-01 | 49028.661 | 61989545.07 | 248199.8233
|  | 2019-01-01 | 4259273.03 | 43599.7332 | 13450751 | 45895.8724 | 2267 | 397881.65 | 44784 | 779 | 0 | 2019-01-01 | 60429.1168
|  | 2019-02-01 | 4544952.29 | 46524.0678 | 9689510 | 33061.984 | 2374 | 367810.95 | 38542 | 580 | 4 | 2019-02-01 | 48570.0066
|  | 2019-03-01 | 5137117.66 | 52585.7248 | 10640588 | 36307.1972 | 2588 | 382708.01 | 56905 | 601 | 0 | 2019-03-01 | 53835.7721
|  | 2019-04-01 | 5327516.18 | 54534.7251 | 6048106 | 20636.9965 | 2436 | 362251.48 | 46157 | 210 | 24 | 2019-04-01 | 38815.2382
|  | 2019-05-01 | 6146168.65 | 62914.8006 | 3954035 | 13491.7289 | 2560 | 373759.47 | 50406 | 26 | 192 | 2019-05-01 | 34463.3291
|  | 2019-06-01 | 6367530.14 | 65180.7511 | 3088513 | 10538.4449 | 2044 | 305405.41 | 32492 | 1 | 226 | 2019-06-01 | 32265.362
|  | 2019-07-01 | 6937601.07 | 71016.24 | 2412562 | 8232.0041 | 2175 | 320463.4 | 45336 | 0 | 405 | 2019-07-01 | 31904.0841
|  | 2019-08-01 | 6938641.05 | 71026.8856 | 2760646 | 9419.7162 | 2253 | 334384.48 | 38273 | 2 | 325 | 2019-08-01 | 33095.3447
|  | 2019-09-01 | 6206459.54 | 63531.9638 | 2368319 | 8081.0407 | 2062 | 299553.43 | 41179 | 8 | 285 | 2019-09-01 | 29258.362
|  | 2019-10-01 | 5299505.14 | 54247.9922 | 4577246 | 15618.2133 | 1794 | 284797.84 | 39458 | 161 | 75 | 2019-10-01 | 33700.8774 | SITE | SITE
|  | 2019-11-01 | 3974166.29 | 40681.2591 | 7651402 | 26107.6701 | 1404 | 202238.94 | 29083 | 627 | 0 | 2019-11-01 | 39668.0898 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2019-12-01 | 3640532.63 | 37266.0429 | 7909828 | 26989.4563 | 1248 | 176427.35 | 23599 | 699 | 0 | 2019-12-01 | 39411.4706 | 64779463.67 | 254380.3248
|  | 2020-01-01 | 3546853.24 | 36307.1007 | 10136628 | 34587.6141 | 1716 | 237911 | 37755 | 708 | 0 | 2020-01-01 | 46689.981
|  | 2020-02-01 | 3851758.86 | 39428.2445 | 8477662 | 28926.9866 | 1557 | 215393 | 38585 | 625 | 0 | 2020-02-01 | 42069.7348
|  | 2020-03-01 | 3738484.75 | 38268.7225 | 5972219 | 20378.0593 | 1514 | 207282 | 25792.1122 | 368 | 20 | 2020-03-01 | 33134.3001
|  | 2020-04-01 | 2781418 | 28471.7795 | 3069175 | 10472.4609 | 424 | 94051 | 12589.2739 | 271 | 5 | 2020-04-01 | 19963.0541
|  | 2020-05-01 | 3630649.4 | 37164.8739 | 1286856 | 4390.9354 | 349 | 57052 | 6105.8219 | 179 | 71 | 2020-05-01 | 16779.2267
|  | 2020-06-01 | 4903768.43 | 50197.0627 | 2807233 | 9578.6776 | 1578 | 211502 | 30682.8561 | 20 | 248 | 2020-06-01 | 26311.0318
|  | 2020-07-01 | 5572275.94 | 57040.1903 | 1722547 | 5877.575 | 1392 | 203237 | 24073.3337 | 0 | 430 | 2020-07-01 | 24890.9717
|  | 2020-08-01 | 5615811.3 | 57485.8368 | 1890143 | 6449.4363 | 1558 | 208968 | 29750.7167 | 0 | 359 | 2020-08-01 | 25611.3819
|  | 2020-09-01 | 4828128.04 | 49422.7754 | 3253472 | 11101.3085 | 1638 | 211315 | 33258.9975 | 63 | 138 | 2020-09-01 | 27575.5669
|  | 2020-10-01 | 4627658.89 | 47370.6878 | 4760664 | 16244.0616 | 1700 | 226848 | 29089.9024 | 157 | 20 | 2020-10-01 | 32034.2908 | SITE | SITE
|  | 2020-11-01 | 4092344.03 | 41890.9768 | 5750945.4 | 19623.0423 | 1408 | 199374 | 34970.7548 | 363 | 6 | 2020-11-01 | 33586.7013 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2020-12-01 | 2504360 | 25635.6958 | 9748423 | 33263.0036 | 1327 | 201607 | 28747.9755 | 762 | 0 | 2020-12-01 | 41808.2355 | 49693510.88 | 200893.1612
|  | 2021-01-01 | 3611280.71 | 36966.6078 | 10899018.8568 | 37189 | 1431 | 212556 | 31583.3535 | 854 | 0 | 2021-01-01 | 49511.2026
|  | 2021-02-01 | 3566421.42 | 36507.409 | 8796820.2965 | 30016 | 1426 | 203966 | 32042.2209 | 733 | 0 | 2021-02-01 | 42185.1363
|  | 2021-03-01 | 4150632.61 | 42487.6436 | 7561818.9395 | 25802 | 1897 | 267730 | 49751.2467 | 457 | 0 | 2021-03-01 | 39964.5479
|  | 2021-04-01 | 4063020.91 | 41590.8129 | 4130250.1479 | 14093 | 1291 | 193896 | 23452.0222 | 275 | 15 | 2021-04-01 | 27956.6043
|  | 2021-05-01 | 4688616.53 | 47994.6762 | 3397865.6222 | 11594 | 1577 | 233091 | 36087.8954 | 102 | 86 | 2021-05-01 | 27592.2254
|  | 2021-06-01 | 5028490.52 | 51473.7711 | 2111576.8336 | 7205 | 1755 | 262256 | 32925.6 | 3 | 254 | 2021-06-01 | 24362.9237
|  | 2021-07-01 | 5561279.19 | 56927.6229 | 1627716.5487 | 5554 | 1287 | 232831 | 33742.6018 | 0 | 375 | 2021-07-01 | 24529.8743
|  | 2021-08-01 | 5612547 | 57452.422 | 1827004.855 | 6234 | 1207 | 245143 | 33539.5624 | 0 | 370 | 2021-08-01 | 25384.8073
|  | 2021-09-01 | 4932260.26 | 50488.7172 | 2302073.0087 | 7855 | 769 | 212941 | 34166.3495 | 25 | 148 | 2021-09-01 | 24684.5724
|  | 2021-10-01 | 4636218.78 | 47458.3105 | 4374964.4651 | 14928 | 783 | 210063 | 18601.2073 | 128 | 57 | 2021-10-01 | 30747.4368 | SITE | SITE
|  | 2021-11-01 | 4192553.82 | 42916.7669 | 10156669.9158 | 34656 | 1387 | 241936 | 42205.2034 | 605 | 0 | 2021-11-01 | 48961.589 | Electric (kWh) | Natural Gas (MMBTU)
|  | 2021-12-01 | 3959841.47 | 40534.6242 | 8372453.4325 | 28568 | 1170 | 231443 | 27641.8183 | 391 | 1 | 2021-12-01 | 42079.5414 | 54003163.22 | 223694
|  | 2022-01-01 | 2176625.88 | 22280.8698 | 13686955 | 56032 | 1097 | 228495 | 22056.4905 | 885 | 4 | 2022-01-01 | 63458.9566 | 52568508.39 | 242537
|  | 2022-02-01 | 3991824 | 40862.011 | 9412822 | 32117.8853 | 1058 | 242442 | 25649.5102 | 622 | 0 | 2022-02-01 | 45738.5556 | 52993910.97 | 244638.8853
|  | 2022-03-01 | 3758008 | 38468.5708 | 7847828 | 26777.9035 | 1599 | 301670 | 42713.6168 | 432 | 0 | 2022-03-01 | 39600.7605 | 52601286.36 | 245614.7888
|  | 2022-04-01 | 4207109 | 43065.76 | 5442310 | 18569.9345 | 1568 | 269688 | 38836.1211 | 238 | 0 | 2022-04-01 | 32925.1878 | 52745374.45 | 250091.7233
|  | 2022-05-01 | 4607630 | 47165.6635 | 4088327 | 13949.9523 | 1620 | 284547 | 49857.3615 | 32 | 144 | 2022-05-01 | 29671.8401 | 52664387.92 | 252447.6756
|  | 2022-06-01 | 5386322 | 55136.6866 | 2686280 | 9165.9688 | 1644 | 289467 | 32553 | 0 | 336 | 2022-06-01 | 27544.8643 | 53022219.4 | 254408.6444
|  | 2022-07-01 | 6048984 | 61919.9771 | 1994634 | 6805.9744 | 1396 | 271948 | 54901 | 0 | 449 | 2022-07-01 | 27445.9668 | 53509924.21 | 255660.6189
|  | 2022-08-01 | 6349929 | 65000.5783 | 2252243 | 7684.9729 | 1561 | 312108 | 45645 | 0 | 358 | 2022-08-01 | 29351.8324 | 54247306.21 | 257111.5918
|  | 2022-09-01 | 5734642 | 58702.2385 | 4013300 | 13693.9495 | 1510 | 293532 | 52668 | 29 | 164 | 2022-09-01 | 33261.3623 | 55049687.95 | 262950.5413
|  | 2022-10-01 | 3282269 | 33598.7037 | 8035686 | 27418.9017 | 1376 | 291765 | 38607 | 259 | 25 | 2022-10-01 | 38618.4696 | 53695738.17 | 275441.443
|  | 2022-11-01 | 4423942 | 45285.3549 | 8898788 | 30363.9283 | 1457 | 288745 | 26495 | 498 | 1 | 2022-11-01 | 45459.0466 | 53927126.35 | 271149.3713
|  | 2022-12-01 | 2719362 | 27836.5479 | 10889973 | 37158.1343 | 877 | 226795 | 25399 | 782 | 0 | 2022-12-01 | 46436.9835 | 52686646.88 | 279739.5055
|  | TOTALS | 578251708.55 | 5919230.8239 | 717742261.4223 | 2458368.6814 | 216796.5 | 32776675.41 | 4289534.9429 | 38993 | 13194
|  |  | 52686646.88 |  |  | 279739.5055
Formulas:
Period = [Actual Date *]

## 5_Estimated vs Actual
5 | ANY SITE
Energy Mapping Process for ANY SITE
|  | Estimated versus Actual |  |  | GRAND TOTALS
This is used to compare you measured and estimated energy consumption at end uses to the actual total energy that you were billed for
For example if your total site electrical bills for the year add up to 65,000,000 kwh, your goal will be for you electrical energy consumption estimate to be close to this same number
The and Mount Holly site energy mapping spreadsheets have a tab for this.
SITE LEVEL
|  |  | ELECTRICITY |  |  |  | CONVERT Electrical to MMBTU
|  |  |  | Total Estimated ANNUAL kWh from Tab 3C: | 62094611.0511 | kWh | 211875.5062 | MMBTU
|  |  |  | Total actual ANNUAL kWh from Duke Energy invoices: | 52686646.88 | kWh | 179774.2153 | MMBTU
2022
|  |  |  | DELTA: | 9407964.1711 | 17.86%
NATURAL GAS
|  |  |  | Total Estimated ANNUAL MMBTU from Tab 3D: | 275251.1278 | MMBTU
|  |  |  | Total actual ANNUAL MMBTU from all natural gas invoices: | 279739.5055 | MMBTU
2022
|  |  |  | DELTA: | -4488.3778 | -1.604%
OTHER COMBUSTION FUELS (LP, Diesel)
|  |  |  | Total Estimated ANNUAL MMBTU from Tab 3D: | 7962 | MMBTU
|  |  |  | Total actual ANNUAL MMBTU from invoices: | 7962 | MMBTU | ESTIMATE
2022
|  |  |  | DELTA: | 0 | 0%
|  |  |  | GRAND TOTAL Estimate: | 495088.6339 | MMBTU
|  |  |  | GRAND TOTAL Actual: | 467475.7208 | MMBTU
2022
|  |  |  | Grand Total DELTA: | 27612.9131 | 5.907%

## 6_Two Key Pies
6 | ANY SITE
Energy Mapping Process for ANY SITE
Create the TWO key Pie Charts
Where does all the energy go? - Continued
|  |  |  | IN | [6 empty] | By INVOICES
[9 empty] | TOTAL energy IN | Type | MMBTU | %
[10 empty] | Liquid Propane | 7769 | 1.662%
[10 empty] | Diesel Fuel | 193 | 0.04129%
[9 empty] | SITE | Electricity | 179774.2153 | 38.46% |  | 64779463.67 | kwh
[10 empty] | Natural Gas | 279739.5055 | 59.84% |  | Actual by Invoice
[11 empty] | 467475.7208 | 100%
|  |  |  | USED | [7 empty] | SORT
[9 empty] | TOTAL energy used from ALL TYPES | By system |  | High to Low
TOTAL
[6 empty] | Energy Type |  |  |  | DEPT | SYSTEM | ESTIMATED
[5 empty] | # | E | NG | LP | D | SORT 1 | SORT 2 | MMBTU | % | Energy Use
[5 empty] | 1 |  | X |  |  | PRODUCTION | PAINT OVENS | 152846 | 32.6% | Paint - OVENS
[5 empty] | 2 | X | X |  |  | FACILITY | BOILER | 107786.28 | 22.99% | Boilers - PROCESS
[5 empty] | 3 | X |  |  |  | PRODUCTION | PAINT FANS | 48014 | 10.24% | Paint - FANS
[5 empty] | 4 | X |  |  |  | FACILITY | PUMPING | 38086 | 8.122% | Facility Pumping
[5 empty] | 5 | X |  |  |  | FACILITY | CHILLER | 37398 | 7.975% | Facility Chillers
[5 empty] | 6 | X | X |  |  | FACILITY | HVAC | 23817 | 5.079% | Facility HVAC
[5 empty] | 7 | X |  | X | X | FACILITY | VEHICLE | 18100 | 3.86% | Facility Vehicles
[5 empty] | 8 | X | X |  |  | FACILITY | BOILER | 9372.72 | 1.999% | Boilers - COMFORT
[5 empty] | 9 | X |  |  |  | FACILITY | COMP AIR | 9317 | 1.987% | Facility Air Compressors
[5 empty] | 10 | X |  |  |  | FACILITY | LIGHT | 7743 | 1.651% | Facility Lighting
[5 empty] | 11 | X |  |  |  | PRODUCTION | PAINT PUMPS | 4548 | 0.9699% | Paint-PUMPS
[5 empty] | 12 | X |  |  |  | PRODUCTION | COMB Blowers | 2778 | 0.5924% | Paint - Oven Comb. Blowers
[5 empty] | 13 | X |  |  |  | FACILITY | COOLIING TOWER | 2676 | 0.5707% | Facility Cooling Towers
[5 empty] | 14 |  | X |  |  | PRODUCTION | PAINT WASHERS | 1968 | 0.4197% | Paint - WASHERS
[5 empty] | 15 | X |  |  |  | FACILITY | EXH FANS | 1817 | 0.3875% | Facility Exh Fans
[5 empty] | 16 |  | X |  |  | FACILITY | HOT WATER | 1282 | 0.2734% | Hot Water
[5 empty] | 17 | X |  |  |  | PRODUCTION | PAINT IR OVEN | 968 | 0.2064% | Paint - IR OVENS
[5 empty] | 18 | X |  |  |  | PRODUCTION | PAINT ROBOTS | 294 | 0.0627% | Paint - ROBOTS
[5 empty] | 19 | X |  |  |  | FACILITY | WWTP | 106 | 0.02261% | Facility WWTP
20
21
[12 empty] | 468917 | 100%
-26171.6339
CHECKs, if ZERO

## 7_SEUs
7 |  | ANY SITE | [8 empty] | From ISO 50001 | 3.5.6 | significant energy use |  | SEU
|  | Energy Mapping Process for ANY SITE | [9 empty] | energy use (3.5.4) accounting for substantial energy consumption (3.5.2) and/or offering considerable potential for energy performance improvement (3.4.6)
Note 1 to entry: Significance criteria are determined by the organization (3.1.1).
|  |  | Determination of SEUs | [8 empty] | Note 2 to entry: SEUs can be facilities, systems, processes, or equipment.
Use the consumption pie chart
|  |  |  | This tab creates a table from the consumption pie chart | [10 empty] | SEU SCORING CRITERIA
|  |  |  | Ranked by total combined energy from all types for specifc energy uses | [9 empty] | Consumption Rank
[16 empty] | Greater than 20% | 10
[10 empty] | Calculated score | [5 empty] | Greater than 15%, but < 20% | 7
|  |  | SORT | [6 empty] | Site scored | [5 empty] | Greater than10%, but < 15% | 5
|  |  | ESTIMATED | [12 empty] | Greater than 1%, but < 10% | 2
|  |  | Annual | [5 empty] | SEU SCORING | Improvement | [5 empty] | Less than 1% | 0.5
|  |  | Consumption | Energy Types Consumed |  |  |  | Consumption | Consumption | Potential | TOTAL | OVERALL
| # | Energy User | (MMBTU) | ELEC | N. Gas | LP | Diesel | Percentage | Rank | Rank | SCORE | RANK |  | Improvement Potential Rank
| 1 | Paint - OVENS | 152846 | - | X | - | - | 32.6% | 10 | 50 | 500 | 1 |  |  | This rank will be entered by the site.
| 2 | Boilers - PROCESS | 107786.28 | X | - | - | - | 22.99% | 10 | 50 | 500 | 1 |  |  | This is based on the perceived or actual level of potential to improve energy performance.
| 3 | Paint - FANS | 48014 | X | - | - | - | 10.24% | 5 | 30 | 150 | 2 |  |  | An energy use with a lower consumption could have an excellent improvement potential.
| 4 | Facility Pumping | 38086 | X | - | - | - | 8.122% | 2 | 30 | 60 |  |  |  | Rank the area from 1 to 10 based on the potential for energy performance improvement.
| 5 | Facility Chillers | 37398 | X | X | - | - | 7.975% | 2 | 30 | 60 |  |  |  |  | Estimated improvement of > 30% to baseline: | 100
| 6 | Facility HVAC | 23817 | X | - | X | X | 5.079% | 2 | 50 | 100 |  |  |  |  | Estimated improvement of 20 - 30% to baseline: | 70
| 7 | Facility Vehicles | 18100 | X | X | - | - | 3.86% | 2 | 30 | 60 |  |  |  |  | Estimated improvement of 10 - 20% to baseline: | 50
| 8 | Boilers - COMFORT | 9372.72 | X | - | - | - | 1.999% | 2 | 50 | 100 |  |  |  |  | Estimated improvement of up to 10% to baseline: | 30
| 9 | Facility Air Compressors | 9317 | X | - | - | - | 1.987% | 2 | 70 | 140 | 3 |  |  |  | Very limited opportunity at this time: | 1
| 10 | Facility Lighting | 7743 | X | - | - | - | 1.651% | 2 | 30 | 60
| 11 | Paint-PUMPS | 4548 | X | - | - | - | 0.9699% | 0.5 | 30 | 15
| 12 | Paint - Oven Comb. Blowers | 2778 | X | - | - | - | 0.5924% | 0.5 | 30 | 15
| 13 | Facility Cooling Towers | 2676 | - | X | - | - | 0.5707% | 0.5 | 30 | 15
| 14 | Paint - WASHERS | 1968 | X | - | - | - | 0.4197% | 0.5 | 50 | 25
| 15 | Facility Exh Fans | 1817 | - | X | - | - | 0.3875% | 0.5 | 50 | 25
| 16 | Hot Water | 1282 | X | - | - | - | 0.2734% | 0.5 | 30 | 15
| 17 | Paint - IR OVENS | 968 | X | - | - | - | 0.2064% | 0.5 | 30 | 15
| 18 | Paint - ROBOTS | 294 | X | - | - | - | 0.0627% | 0.5 | 30 | 15
| 19 | Facility WWTP | 106 | - | - | - | - | 0.02261% | 0.5 | 30 | 15
| 20 |  | 0 | - | - | - | - | 0%
|  |  | 468917 |  |  |  |  | 100%
|  |  | CHECK |  |  |  |  | CHECK
SELECTED SEUs
|  |  |  | 1 | Paint OVENS and related processes | [5 empty] | 45.09% | of total site energy
|  |  |  | 2 | Boilers - Process
|  |  |  | 3 | MAYBE - Air Compressors
|  |  | NOTE: | The Selected SEUs table above is filled out through discussion and agreement of the Energy Team

## 7A_SEU Actions
7A |  | YOUR SITE: |  |  | REFERENCE INFORMATION
Follow on actions REQUIRES for your selected SEUs.
|  |  | Significant Energy Uses (SEUs) |  |  | UPDATED for ISO 50001: 2018
The ISO 50001: 2018 standard requires you to identify SEUs for your plant operations.
Once you have designated these SEUs, there are additional requirements for work to be done for each of these SEUs.
|  |  | DEFINITION | 3.5.6 significant energy use (SEU)
|  |  | from the ISO 50001: | energy use (3.5.4) accounting for substantial energy consumption (3.5.2) and/or offering considerable potential for energy performance improvement (3.4.6)
|  |  | 2018 Standard | Note 1 to entry: Significance criteria are determined by the organization (3.1.1).
Note 2 to entry: SEUs can be facilities, systems, processes, or equipment.
| Item | PDCA | 50001 Ready | ISO 50001
| # | Step | Step(s) | Section | Direct Text from the ISO 50001: 2018 Standard | Comments
| 1 | PLAN | 12 | 6.2 Objectives, energy targets and planning to achieve them | 6.2.2 The objectives and energy targets shall: a) …. d) consider SEUs (see 6.3) | You must consider and take in to account its SEUs when deciding and establishing the objectives and energy targets. It would make sense that some of the objectives and energy targets are specifically aimed at improvements for specific SEUs.
| 2 | PLAN | 8, 9 | 6.3 Energy review | The organization shall develop and conduct an energy review. To develop the energy review, the organization shall: a) …. b) based on the analysis, identify SEUs (see 3.5.6); c) for each SEU: 1) determine relevant variables; 2) determine current performance; 3) identify the person(s) doing work under its control that influence or affect the SEUs; | The plant energy review and energy balance will help to find the SEUs. All energy sources must be considered. SEUs can be facilities, systems, processes, or equipment. Relevant variables are things like production volume, cooling degree days, heating degrees days, etc. You must know how much energy your SEUs are consuming down to the equipment level and you must estimate future energy use and consumption for all SEUs. You must know who is working with your SEUs.
| 3 | PLAN | 8 | 6.6 Planning for collection of energy data | Data to be collected (or acquired by measurement as applicable) and retained documented information (see 7.5) shall include: a) the relevant variables for SEUs; b) energy consumption related to SEUs and to the organization; c) operational criteria related to SEUs; | You must determine relevant variables such as production volume, cooling degree days, heating degrees days, etc., for all SEUs. You must collect and retain consumption data on all SEUs. You must intergrate your SEUs with you operational and maintenance criteria.
| 4 | DO | 17 | 8.1 Operational planning and control | The organization shall plan, implement and control the processes, related to its SEUs (see 6.3), needed to meet requirements and to implement the actions determined in 6.2, by: a) establishing criteria for the processes, including the effective operation and maintenance of facilities, equipment, systems and energy-using processes, where their absence can lead to a significant deviation from intended energy performance; b) communicating (see 7.4) the criteria to relevant person(s) doing work under the control of the organization; c) implementing control of the processes in accordance with the criteria, including operating and maintaining facilities, equipment, systems and energy-using processes in accordance with established criteria; d) keeping documented information (see 7.5) to the extent necessary to have confidence that the processes have been carried out as planned. The organization shall control planned changes and review the consequences of unintended changes, taking actions to mitigate any adverse effects, as necessary. The organization shall ensure that outsourced SEUs or processes related to its SEUs (see 6.3) are controlled (see 8.3). | Operational and maintenance controls, activities and criteria are centered around your selected SEUs. Absence of these controls could lead to problems with the performance of the SEUs. This must be monitored and tracked, and records kept. Significant deviations must be defined. Once the criteria and activities are set up, they must be followed. You must inform, train, or make aware all relevant person(s) who carry out these controls on the SEUs. Documented information must be maintained on the above actions. The above includes outsourced SEUs and processes related to SEUs.
| 5 | DO | 19 | 8.3 Procurement | When procuring energy using products, equipment and services that have, or can have, an impact on SEUs, the organization shall inform suppliers that energy performance is one of the evaluation criteria for procurement. | You must inform suppliers that energy performance is part of the procurement evaluation process for anything that is purchased that can have an impact on an SEU. This can take the form of a letter or an email to selected suppliers. Records of this action should be maintained as evidence of completion.
| 6 | CHECK | 20, 21 | 9.1 Monitoring, measurement, analysis and evaluation of energy performance and the EnMS | 9.1.1 General The organization shall determine for energy performance and the EnMS: a) what needs to be monitored and measured, including at a minimum the following key characteristics: 1) 2) 3) operation of SEUs; 4) | The operation of SEUs must be part of the overall monitoring plan for the organization. The methods for monitoring, measuring, analyzing and evaluating data related to SEUs must be determined. When monitoring and measurement of data related to SEUs occurs must be determined. When analysis and evaluation of data related to SEUs occurs must be determined. Results of the above actions must be part of the organization's documented information.

## 8_Energy IMPV
8 | YOUR SITE: | [5 empty] | From ISO 50001 | 6.3 Energy review
|  | Energy Improvement Project Evaluation |  | TASK 10 |  |  |  | The organization shall develop and conduct an energy review.
|  | List and Rank Energy Improvement Projects based on SEUs and other factors | [5 empty] | To develop the energy review, the organization shall:
|  | Use SEU pie chart and other inputs for generating ideas for energy improvements | [5 empty] | a), b), c), …..
d) determine and prioritize opportunities for improving energy performance;
[21 empty] | EVALUATION CRITERIA and SCORING (5 = BEST) | [5 empty] | Criteria Scoring Details BELOW** |  |  | Pull Down Menu | Pull Down Menu | FOLLOW UP
| Project ID# | Performance Improvement Opportunity Name | Performance Improvement Opportunity Description | Related to a Significant Energy User (SEU)? Which One? | Part of Energy Target (Enter Name) - Optional | Responsible Lead Person (Name) | Date Entered | Estimated Annual Savings (should have back up calculation available) | [7 empty] | Non-Energy Benefits (list name and estimated value, if known) |  |  |  | Estimated Project Cost | 1. Project COST | 2. Simple Payback | 3. Implementation Time | 4. Non-Energy Benefits | 5. Plant Employee Impact | 6. Add OTHER | 7. Add OTHER | 8. Add OTHER | Opportunity Score (multiply) | Prioritization Level | Implementation Status | Project Completion Date | Actual Annual Savings | [7 empty] | Actual Non-Energy Benefits Realized |  |  |  | Actual Implementation Cost
[8 empty] | Electricity (kWh) | Natural Gas (therms) | Liquid Propane (gallons) | Diesel Fuel (gallons) | Other Fuel Oils (gallons) | Other | Other | Other | 1 | 2 | 3 | 4 |  | Lower = 5 Higher = 1 | Lower = 5 Higher = 1 | Shorter = 5 Longer = 1 | More = 5 Less = 1 | Higher = 5 Lower = 1 | Best= 5 Worst= 1 | Best= 5 Worst= 1 | Best= 5 Worst= 1 |  |  |  |  | Electricity (kWh) | Natural Gas (therms) | Liquid Propane (gallons) | Diesel Fuel (gallons) | Other Fuel Oils (gallons) | Other | Other | Other | 1 | 2 | 3 | 4
EXAMPLE | EEM# 29 | Chilled Water Pump VFDs | Add VFDs and controls to the chilled water primary supply pump motors, eight motors at 50 hp each | YES, Chillers | Improve Overall HVAC Energy Consumption | M. Stowe | 2020-04-21 | 475000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Reduce chiller condenser water make up by ~ 15% | Improve consistency of plant air temperature and humidity |  |  | 17500 | 4 | 5 | 3 | 1 | 3 | x | x | x | 180 | High | Completed | 2020-07-12 | TBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Reduced chiller condenser water make up by ~ 18% | Improved consistency of plant air temperature and humidity |  |  | 16785
0
0
0
0
0
0
0
**Scoring Criteria Details
[21 empty] | 1. Project COST ($) |  |  | 5. Plant Employee Impact |  | Empolyee Impact Definitions
[21 empty] | $5,000 or less | 5 |  | Significant | 5 | Significant | Good | Some | Limited | No Impact
[21 empty] | > $5,000 up to $50,000 | 4 |  | Good | 4 | Employees have a direct and substantial impact on the successful implementation of the energy project | Employees still have a direct, but less substantial impact on the successful implementation of the energy project | Employees still have some, but a much less substantial impact on the successful implementation of the energy project | Employees have limited impact on energy project success because the new system is mostly automated and needs very little human interface | The energy project deploys a fully automated systems with very little to no human interface.
[21 empty] | > $50,000 up to $500,000 | 3 |  | Some | 3
[21 empty] | > $500,000 up to $1,000000 | 2 |  | Limited | 2
[21 empty] | > $1,000,000 | 1 |  | No impact | 1
[21 empty] | 2. Simple Payback (years) |  |  |  |  | Project EXAMPLES: Compressed air leak repair Equipment start up and shut down optimization Behaviorial based projects like turning off lights and computers | Project EXAMPLES: Installing an automated control system where employees still have a good amount of input Implementing condenser water reset for chillers | Project EXAMPLES: Installing VFDs on pump and fan motors that will general operate automatically, but still require set up, system operation, and periodic adjustments by technicians | Project EXAMPLES: Installing a VFD air compressor that automatically starts and loads up and down based on plant air pressure | Project EXAMPLES: Installing a fully automated building control system that, once set up, pretty much runs on its own
[21 empty] | 2 years or less | 5
[21 empty] | > 2 up to 3 years | 4
[21 empty] | > 3 up to 4 years | 3
[21 empty] | > 4 up to 5 years | 2
[21 empty] | > 5 years | 1
3. Implementation Time (years)
[21 empty] | 6 months or less | 5 |  | Add Others
[21 empty] | > 6 month up to 1 year | 4 |  |  | 5
[21 empty] | > 1 year up to 3 years | 3 |  |  | 4
[21 empty] | > 3 years up to 5 years | 2 |  |  | 3
[21 empty] | > 5 years | 1 |  |  | 2
1
4. Non-Energy Benefits
[20 empty] | From the list below: | > 4 | 5
[21 empty] | Up to 4 | 4
[21 empty] | Up to 3 | 3
[21 empty] | Up to 2 | 2
[21 empty] | NONE | 1
NON-Energy Benfits List
Productivity improvements
Quality improvements
Ergonomic improvements
Better material flow
Labor savings
Scrap reduction
Reduce overtime
Water use reduction
Waste reduction
Emissions reduction
Pollution reduction
Permitting requirements reduced
Employee work condition improvements
Operational safety improvements
Better floor space utilization
Carbon footprint reduction
Greenhouse gas reduction
Public relations improved
Brand enhancement
Please add more, as needed
Note on X7: Author: Include potential equipment repair expenses here, as needed.
Note on Y7: Author: Include potential equipment repair expenses here, as needed.
Note on AA7: Author: Refer to non energy benefits section of this tab at columns "S" thru "V" and the table below
Note on AF7: Author: Formula is currently set up to multiply the first FIVE scores. If you add criteria 6, 7, or 8, than add these to the formula. Also, if desired, you can make this a weighted formula, e.g. to give say, cost a 50% weighting, etc.

## 9_Action Plan Template
9 |  | YOUR SITE: |  |  |  | TASK 13 | [5 empty] | From ISO 50001 | 6.2.3 When planning how to achieve its objectives and energy targets, the organization shall establish and maintain action plans that include:
|  |  | Energy Mapping Process for YOUR SITE | [10 empty] | — what will be done;
|  |  | Use the template below to develop action plans for energy improvement projects from Tab 8. | [10 empty] | — what resources will be required;
— who will be responsible;
— when it will be completed;
— how the results will be evaluated, including the method(s) used to verify energy performance improvement (see 9.1).
Energy Management Action Plan Template (print out, fill out, and retain) | [12 empty] | The organization shall consider how the actions to achieve its objectives and energy targets can be integrated into the organization’s business processes. The organization shall retain documented information on action plans (see 7.5).
| Project Objective/Target: | [16 empty] | Planned Completion Date:
Actual Completion Date:
Project Description:
| Project Budget: | [8 empty] | Project Leader:
| Actual Cost: | [8 empty] | Management Review:
Project Planning
| Action Items | [6 empty] | Leader Position |  |  |  | Due Date |  |  | Completion Date |  | Required Resources/Comments
Project Results Verification
Describe the method(s) to be used to verify the results of the action plan and the energy performance improvement achieved:
| Unit(s) of Measurement |  |  |  | Pre-Project Value |  | Post Project Value |  | Net Change |  | Source of Measurement | [7 empty] | Date Done | Responsible Party
(e.g. meter ID, calculation formula, etc.)
Evaluation of Results:
Communication/Training Plan: Identify departments affected by the project. 1) Mark the first column for departments involved with/affected with the project implementation with a capital "I" 2) Mark the second column for departments involved with/affected by sustaining the project improvements with a capital "S"
| All Departments | [5 empty] | Production | [8 empty] | Lab
| Sales/Marketing | [5 empty] | Maintenance | [8 empty] | Purchasing
| Accounting | [5 empty] | Transportation | [8 empty] | Bldg./Facility Ops & Mgt
| Human Resources | [5 empty] | Warehouse | [8 empty] | Corporate
| Customer Service | [5 empty] | Custodial/Housekeeping | [8 empty] | Contractors
Sustaining the project improvements
Document the details for each responsibility necessary to sustain the energy savings achieved by the project’s implementation.
| Item |  | Leader Position | What needs to be done?, i.e. tasks/assignments for this item
Roles
Resources
Communication
Training
Oper. Controls
Monitoring & Measurement
Process Changes
Project Follow-up Notes/Lessons Learned

## 10_Operational Controls
10 |  | YOUR SITE: |  |  |  | From ISO 50001 | 8.1 Operational planning and control
|  | Operation Controls Planning Template |  |  |  |  | The organization shall plan, implement and control the processes, related to its SEUs, needed to meet requirements, and to implement the action plans by:
a) establishing criteria for the processes, including the effective operation and maintenance of facilities, equipment, systems and energy-using processes, where their absence can lead to a significant deviation from intended energy performance;
|  |  | EXAMPLE | [5 empty] | NOTE: Significant deviation criteria are determined by the organization.
b) communicating the criteria to relevant person(s) doing work under the control of the organization;
c) implementing control of the processes in accordance with the criteria, including operating and maintaining facilities, equipment, systems and energy-using processes in accordance with established criteria;
d) keeping documented information (see 7.5) to the extent necessary to have confidence that the processes have been carried out as planned.
The organization shall control planned changes and review the consequences of unintended changes, taking actions to mitigate any adverse effects, as necessary.
The organization shall ensure that outsourced SEUs or processes related to its SEUs are controlled (see 8.3).
| YOUR SITE Operational & Maintenance Controls Planning Worksheet | [25 empty] | NOTE: Once the Operational controls and maintenance criteria are identified, they must be communicated to the appropriate personnel and implemented
|  | USE for both SEUs and/or Action Plans (APs) | [13 empty] | UCL = Upper Control Limit |  |  |  |  | Focus on biggest energy
SEU or AP # |  | Short Name | [14 empty] | LCL = Lower Control Limit |  |  |  | consumers FIRST
SEU #1 |  | COOLING | Associated with this SEU |  |  |  | Energy Types Consumed by this SEU | BRAINSTORM Operational Controls |  |  | Identify Additional Information for Selected Parameters | [7 empty] | Parameter Monitoring | [5 empty] | Identify Maintenance Criteria |  | Communicate to the Appropriate Personnel |  |  |  |  | Implement the Selected Operational Controls and Maintenance Criteria |  |  |  | Process for Managing Changes
|  | Full Description | Facilities | Processes | Systems | Equipment |  |  |  |  | Parameter | Instrument | Calibration Required? | Units | Value | UCL | LCL | Energy Impact Trend | WHO? | WHAT? | WHERE? | WHEN? | HOW? | Action for Data | Describe the maintenance system for the SEU system including who, what, where, when, and how: |  | Role |  | Group | X | Methods (mark all used) | Decide on Implementation Tools |  | X | Implementation Tools (mark all used)
|  | Building Cooling | Central Energy Plants | Vapor compression | Chilled Water | Chillers-Water cooled | Electricity | What system parameters can impact the energy consumption of this SEU/Action Plan? (list) |  |  | Chilled water return temperature | Temperature Gauge | YES | ◦F | 55 | 59 | 51 | Higher indicates more cooling load | DPW O&M Techs | Temperatures | Central Energy Plants | Temperatures: Hourly | Log sheets | Send log sheets and data downloads to the Energy Team Leader at DPW. The Energy Team Leader and REMs will review and analyze the data, and give feedback on any action needed to the O&M teams. | All equipment related to the COOLING SEU is properly maintained per manufacturer's recommendations using the XYZ Maintenance Management System. PM work orders are issued based on the periodicity of the PM item and PMs are then scheduled and completed. Records of completed PMs are maintained by DPW. ....AND SO ON... |  | Equipment Operators |  | DPW | X | Shift or toolbox meetings | 1) For each selected implementation tool: |  |  | Work instructions | 1) BRAINSTORM with the Team:
|  | Equipment Cooling | Individual Buildings | Thermodynamics | Condenser Water | Chiller Compressors |  | Chilled water return temperature |  | Chiller sequencing program | Chilled water supply temperature | Temperature Gauge | YES | ◦F | 45 | 47 | 43 | Lower takes more energy to create | Honeywell Operators | T-Stat Setpoints | Individual Buildings | T-Stat Setpoints: | Building automation sys. | [5 empty] | Honeywell | X | Demonstrations |  | a) Create the tool, if needed | X | Standard Operating Procedures (SOPs) |  | a) What unplanned changes could occur to impact this SEU energy performance:
|  |  | Data Centers | Pumping | HVAC | Chilled Water Pumps |  | Chilled water supply temperature |  | Building automation setpoints | Condenser water supply temperature | Temperature Gauge | YES | ◦F | 65 | 78 | 65 | Cooler makes the chiller more efficient | Facility Managers |  | Commands | Periodically (TBD) | [6 empty] | JCI |  | E-mails |  | b) Include the tool in document control, as needed | X | Log sheets |  |  | Examples:
|  |  | Dining Facilities |  | (Ventilation) | Condenser Water Pumps |  | Condenser water supply temperature |  | Air handling unit outside air dampers | Thermostat settings | Variety of Thermostats |  | ◦F | 74 | n/a | n/a | Lower setting will require more cooling | Building Energy Managers |  | Barracks | [9 empty] | Staff meetings |  | c) Train personnel on how to use the tool |  | Logbooks |  |  | Random people adjusting thermostats
|  |  | Commissaries |  | (Air Conditioning) | Cooling Towers |  | Thermostat settings |  | Chiller loading / unloading (i.e. cycling) | etc. | [7 empty] | Others |  | Dining Facilities | 24 x 7 |  |  |  |  | Maintenance Technicians |  | DPW | X | Equipment markings |  | d) Start using the tool |  | Checklist |  |  | Setpoints on equipment changed without approval
[5 empty] | Humidity Control | Cooling Tower Fans |  | Control valve positions |  | Heating and cooling at the same time | OTHERS? | [9 empty] | Others | [7 empty] | Honeywell |  | Supplier meetings |  | e) Collect data from the tool | X | Work area postings |  |  | Some function bypassed
[5 empty] | Controls | Chillers-Air cooled |  | VFD settings | [20 empty] | JCI | X | Contractor briefings |  | f) Follow up to make sure the tool is effective | X | Signs and labeling |  | b) How can these be avoided | VFD setting changed
[5 empty] | Instrumentation | Other pumps |  | Which of these parameters can be readily monitored, measured, and controlled? (list) | [21 empty] | X | On-the-job training |  | g) Follow up to make sure the tool is being used properly |  | Specific personnel certifications |  |  | Not completing a required PM item
[5 empty] | Two-Pipe Systems | Other Fans | [20 empty] | Building Managers |  | DPW | X | Shift training |  | h) Periodically review and update tools |  | Brochures and other visual aids |  |  | Removing a critical sensor
[5 empty] | Four-Pipe Systems | Air Handling Units | [22 empty] | Bragg Site | X | Classroom training |  |  |  | Templates
[6 empty] | Cooling Coils | [19 empty] | Typical maintenance items include: |  |  | Commands |  | Supplier training |  |  | X | Statistical Process Control (SPC) charts | 2) When changes are required:
[6 empty] | Control Valves | [19 empty] | Lubrication |  |  |  | X | Peer mentoring |  |  | X | Building automation systems |  | a) Document the change
[6 empty] | Heat Exchangers | [19 empty] | Filter replacement | Operational and Maintenance |  |  |  | On-line training |  |  |  | Spreadsheets |  | b) Communicate the change to appropriate personnel
[6 empty] | VFDs | [19 empty] | Tension adjustment |  | Leaders | DPW |  | Training from certified bodies | [5 empty] | c) Update implementation tools, as needed
[8 empty] | Selected parameters for this SEU/Action Plan (list) | [17 empty] | Cleaning |  |  | Honeywell | X | Technical training | [5 empty] | d) Follow up to ensure that the change is effective and working well
[26 empty] | Leak repair |  |  | JCI
Fluid levels
[26 empty] | Thermography | Others:
Vibration analysis
[16 empty] | UCL = Upper Control Limit | [9 empty] | Tuning, etc. |  |  |  |  | ADD OTHERS, as needed |  |  |  | ADD OTHERS, as needed
SEU or AP # |  | Short Name | [14 empty] | LCL = Lower Control Limit
SEU #2 |  | HEATING | Associated with this SEU |  |  |  | Energy Types Consumed by this SEU | BRAINSTORM Operational Controls |  |  | Identify Additional Information for Selected Parameters | [7 empty] | Parameter Monitoring | [5 empty] | Identify Maintenance Criteria |  | Communicate to the Appropriate Personnel |  |  |  |  | Implement the Selected Operational Controls and Maintenance Criteria |  |  |  | Process for Managing Changes
|  | Full Description | Facilities | Processes | Systems | Equipment |  |  |  |  | Parameter | Instrument | Calibration Required? | Units | Value | UCL | LCL | Energy Impact Trend | WHO? | WHAT? | WHERE? | WHEN? | HOW? | Action for Data | Describe the maintenance system for the SEU system including who, what, where, when, and how: |  | Role |  | Group | X | Methods (mark all used) | Decide on Implementation Tools |  | X | Implementation Tools (mark all used)
|  | Building Heating | Central Energy Plants | Combustion | MTHW | Boilers | Electricity | What system parameters can impact the energy consumption of this SEU/Action Plan? (list) | [22 empty] | Shift or toolbox meetings | 1) For each selected implementation tool: |  |  | Work instructions | 1) BRAINSTORM with the Team:
|  | Water Heating | Individual Buildings | Thermodynamics | LTHW | Combustion Burners | Natural Gas | MTHW supply temperature |  | Combustion burner settings | [20 empty] | Demonstrations |  | a) Create the tool, if needed |  | Standard Operating Procedures (SOPs) |  | a) What unplanned changes could occur to impact this SEU energy performance:
|  |  | Barracks | Pumping | HVAC | Combustion Blowers | #2 Fuel Oil | LTHW supply temperature |  | Flue exhaust oxygen level | [20 empty] | E-mails |  | b) Include the tool in document control, as needed |  | Log sheets |  |  | Examples:
|  |  | Dining Facilities |  | (Heating) | Hot Water Pumps |  | Thermostat settings |  | Percent excess air to burners | [20 empty] | Staff meetings |  | c) Train personnel on how to use the tool |  | Logbooks |  |  | Random people adjusting thermostats
[5 empty] | Controls | Feed Water Pumps |  | Control valve positions |  | Boiler loading / loading (i.e. cycling) | [20 empty] | Equipment markings |  | d) Start using the tool |  | Checklist |  |  | Setpoints on equipment changed without approval
[5 empty] | Instrumentation | Fans |  | VFD settings |  | Heating and cooling at the same time | [20 empty] | Supplier meetings |  | e) Collect data from the tool |  | Work area postings |  |  | Some function bypassed
[5 empty] | Two-Pipe Systems | Other Pumps | [24 empty] | Contractor briefings |  | f) Follow up to make sure the tool is effective |  | Signs and labeling |  | b) How can these be avoided | VFD setting changed
[5 empty] | Four-Pipe Systems | Direct Fired Heating |  | Which of these parameters can be readily monitored, measured, and controlled? (list) | [22 empty] | On-the-job training |  | g) Follow up to make sure the tool is being used properly |  | Specific personnel certifications |  |  | Not completing a required PM item
[6 empty] | Air Handling Units | [24 empty] | Shift training |  | h) Periodically review and update tools |  | Brochures and other visual aids |  |  | Removing a critical sensor
[6 empty] | Heating Coils | [24 empty] | Classroom training |  |  |  | Templates
[6 empty] | Heat Exchangers | [19 empty] | Typical maintenance items include: |  |  |  |  | Supplier training |  |  |  | Statistical Process Control (SPC) charts | 2) When changes are required:
[6 empty] | Control Valves | [19 empty] | Lubrication |  |  |  |  | Peer mentoring |  |  |  | Building automation systems |  | a) Document the change
[6 empty] | VFDs | [19 empty] | Filter replacement |  |  |  |  | On-line training |  |  |  | Spreadsheets |  | b) Communicate the change to appropriate personnel
[26 empty] | Tension adjustment |  |  |  |  | Training from certified bodies | [5 empty] | c) Update implementation tools, as needed
[8 empty] | Selected parameters for this SEU/Action Plan (list) | [17 empty] | Cleaning |  |  |  |  | Technical training | [5 empty] | d) Follow up to ensure that the change is effective and working well
Leak repair
Fluid levels
Thermography
Vibration analysis
[16 empty] | UCL = Upper Control Limit | [9 empty] | Tuning, etc. |  |  |  |  | ADD OTHERS, as needed |  |  |  | ADD OTHERS, as needed
SEU or AP # |  | Short Name | [14 empty] | LCL = Lower Control Limit
SEU #3 |  | LIGHTING | Associated with this SEU |  |  |  | Energy Types Consumed by this SEU | BRAINSTORM Operational Controls |  |  | Identify Additional Information for Selected Parameters | [7 empty] | Parameter Monitoring | [5 empty] | Identify Maintenance Criteria |  | Communicate to the Appropriate Personnel |  |  |  |  | Implement the Selected Operational Controls and Maintenance Criteria |  |  |  | Process for Managing Changes
|  | Full Description | Facilities | Processes | Systems | Equipment |  |  |  |  | Parameter | Instrument | Calibration Required? | Units | Value | UCL | LCL | Energy Impact Trend | WHO? | WHAT? | WHERE? | WHEN? | HOW? | Action for Data | Describe the maintenance system for the SEU system including who, what, where, when, and how: |  | Role |  | Group | X | Methods (mark all used) | Decide on Implementation Tools |  | X | Implementation Tools (mark all used)
|  | Site-wide | All buildings on site | Illumination | Lighting circuits | Fixtures | Electricity | What system parameters can impact the energy consumption of this SEU/Action Plan? (list) | [22 empty] | Shift or toolbox meetings | 1) For each selected implementation tool: |  |  | Work instructions | 1) BRAINSTORM with the Team:
|  | Indoor |  |  | Controls | Lamps |  | Time that the lights are on, especially when not needed | [22 empty] | Demonstrations |  | a) Create the tool, if needed |  | Standard Operating Procedures (SOPs) |  | a) What unplanned changes could occur to impact this SEU energy performance:
|  | Outdoor |  |  |  | Occupancy Sensors |  | Proper operation of occupancy and daylight sensors | [22 empty] | E-mails |  | b) Include the tool in document control, as needed |  | Log sheets |  |  | Examples:
[6 empty] | Timers | [24 empty] | Staff meetings |  | c) Train personnel on how to use the tool |  | Logbooks |  |  | Random people adjusting thermostats
[6 empty] | Daylight Sensors | [24 empty] | Equipment markings |  | d) Start using the tool |  | Checklist |  |  | Setpoints on equipment changed without approval
[31 empty] | Supplier meetings |  | e) Collect data from the tool |  | Work area postings |  |  | Some function bypassed
[31 empty] | Contractor briefings |  | f) Follow up to make sure the tool is effective |  | Signs and labeling |  | b) How can these be avoided | VFD setting changed
[8 empty] | Which of these parameters can be readily monitored, measured, and controlled? (list) | [22 empty] | On-the-job training |  | g) Follow up to make sure the tool is being used properly |  | Specific personnel certifications |  |  | Not completing a required PM item
[31 empty] | Shift training |  | h) Periodically review and update tools |  | Brochures and other visual aids |  |  | Removing a critical sensor
[31 empty] | Classroom training |  |  |  | Templates
[26 empty] | Typical maintenance items include: |  |  |  |  | Supplier training |  |  |  | Statistical Process Control (SPC) charts | 2) When changes are required:
[26 empty] | Lubrication |  |  |  |  | Peer mentoring |  |  |  | Building automation systems |  | a) Document the change
[26 empty] | Filter replacement |  |  |  |  | On-line training |  |  |  | Spreadsheets |  | b) Communicate the change to appropriate personnel
[26 empty] | Tension adjustment |  |  |  |  | Training from certified bodies | [5 empty] | c) Update implementation tools, as needed
[8 empty] | Selected parameters for this SEU/Action Plan (list) | [17 empty] | Cleaning |  |  |  |  | Technical training | [5 empty] | d) Follow up to ensure that the change is effective and working well
Leak repair
Fluid levels
Thermography
Vibration analysis
[26 empty] | Tuning, etc. |  |  |  |  | ADD OTHERS, as needed |  |  |  | ADD OTHERS, as needed
NOTE:
Work through this brainstorming exercise with your DPW O&M teams and contractors, especially Honeywell and SELECT your parameters for every SEU.
NOTE:
Operational controls establish criteria to monitor to optimize the energy performance of an SEU. The absence of these operational control parameters can lead to a significant deviations from intended energy performance.
Imagine how chiller energy consumption would be impacted if there were no controls on thermostats!
NOTE:
Examples of significant deviation include:
Systems running outside of control limits
Energy consumption varies unexpectedly
Change in efficiency
Increased maintenance requirements
Increased equipment downtime
Increased in equipment load time
Longer run times
Need to change settings frequently
NOTE:
Possible sources for finding operational control criteria:
Manufacturer’s recommendation
Equipment technical manuals
Subject Matter Experts
Minimum process or system requirements
Service personnel suggested operating settings
Statistical process controls
Benchmarking performance of similar equipment
Industry standards
NOTE:
This section identifies details on the process for monitoring the selected parameters:
WHO? = Who monitors the parameter and collects information?
WHAT? = What specific information is collected?
WHERE? = Where on site, within the scope of the EnMS are systems located that need the monitoring?
WHEN? = When is data collected and recorded?
HOW? = How is the data collected? Is this a manual pen & paper process or is this information recorded in a building automation system, etc.
Action for data: Once the data is collected, what is done with it. Where is the data stored? Who gets the data? Who aggregates the data Who analyzes the data? Who issues actions based on the data analysis?
NOTE:
In addition to the operational controls, SEUs must also receive proper maintenance. This should already be in place for the SEU equipment. For the EnMS there must be specific maintenance criteria in the form of a preventative maintenance system (PMS) with daily, weekly, monthly, annual, etc. periodic maintenance items to be competed on the SEU systems. Records of the scheduling and completion of these PMS items must be kept.
NOTE:
Once identified, it is very important to communicate these selected operational controls and maintenance criteria to the appropriate personnel.
Appropriate personnel should include operators and maintenance technicians for the equipment and systems designated as SEUs. This must include site personnel and contractors. Leadership for these personnel should also be in the loop for this.
Communications should include the operational controls and maintenance criteria identified in the previous columns of the planning worksheet, or basically who, what, when, where, how, how often, records, documentation, and response to signification deviations.
Any forms, log sheets, building automation systems, etc., that will be used should be included in these communications.
NOTE:
Closely tied to the communication of operational controls and maintenance criteria are the implementation tools.
The energy team and the equipment operators, maintenance techs, and others should work together to develop and issue the forms, log sheets, building automation systems, etc., that will be used for monitoring and completing operational controls and maintenance criteria.
NOTE:
The key point here are:
- Anticipate unplanned changes that may occur and avoid these
- Train personnel NOT to randomly change critical operational control parameters without approval
- When changes are needed, follow the process for completing the change

## 99A_Baseline&Achievement
99A
Baseline and Achievement Period Examples for Energy Improvement
Reference Info
Relationship between
|  |  | Baseline Period |  |  | Must be at least 12 months long
|  |  | Achievement Period |  |  | Starts at the end of the Baseline Period and must be at least 12 months long, but no more that 120 months long
|  |  | Reporting Period |  |  | Must be at least 12 months long
Achievement Period and Reporting Period must END at the same time
Achievement Period does NOT have to be a multiple of 12 months, although this is convenient
Examples:
|  | #1 | Shortest Possible Scenario
|  | Baseline Period | 12 | months
|  | Achievement Period | 12 | months
|  | Reporting Period | 12 | months
Reporting Period
| Baseline Period |  |  |  | Achievement Period
| 2014-01-01 |  |  |  | 2015-01-01 |  |  | 2016-01-01
|  | #2 | Typical Scenario
|  | Baseline Period | 12 | months
|  | Achievement Period | 36 | months
|  | Reporting Period | 12 | months
Reporting Period
| Baseline Period |  |  |  | Achievement Period
| 2014-01-01 |  |  |  | 2015-01-01 |  |  | 2016-01-01 |  | 2017-01-01 |  | 2018-01-01
|  | #3 | Very Long Scenario
|  | Baseline Period | 12 | months
|  | Achievement Period | 120 | months
|  | Reporting Period | 12 | months
Reporting Period
| Baseline Period |  | Achievement Period
| 2014-01-01 |  | 2015-01-01 |  | 2016-01-01 |  | 2017-01-01 | 2018-01-01 | 2019-01-01 | 2020-01-01 | 2021-01-01 | 2022-01-01 | 2023-01-01 | 2024-01-01 | 2025-01-01

## 99B_Bottom Up Graphic
99B
Bottom Up Energy Savings Example Graphic
Reference Info
| Top-Down Energy Savings, using the model | [6 empty] | Bottom-Up Energy Savings, using the Registry
Project 6
TD Total Energy Savings
|  |  | Total Energy Used (THEN) |  |  | ESPTD
[7 empty] | Should be close |  |  |  | Project 5
Project 4
BU Total Energy Savings
[9 empty] | ESPBU |  | Project 3
Project 2
Total Energy Used (NOW)
Project 1
RF = ESPBU / ESPTD