## Instructions
Chilled Water System Scoping Tool (CWST)
Color Legend
Orange | User Input / Choose Value
Green | User Input / Numeric / Text
Grey | Intermediate/ Calculation
Objective/Intended Use Notes:
The tool uses two evaluation question sets to infer the general energy efficiency potential of a facility. The first set of questions requires users to input company and plant level information that includes the background information, industry sector, and application type. This information is used to determine the fraction of energy consumed for process cooling compared to overall energy consumed by the plant. Then the user is asked about general plant-level operations and bestpractices. The second level of questionnaire is more detailed and looks at individual equipment and their operations in the system. The tool uses information from these questionnaires to evaluate operating practices and general upkeep of the individual equipment. Based on the answers provided the tool assigns highest scores to most efficient equipment and practices and lower scores to less efficient equipment or practice. This allows the tool to estimate the level of energy efficiency opportunity present in the system.
Instructions for filling out details:
1. Please use the color legend indicated above to input answers to the questions indicated. 2. Include information for all chilled water plant system equipment such as compressors, evaporators, condensers, cooling towers, heat exchangers, associated fans and pumps etc.
Disclaimer:
This scoping tool is created as a supplemental guidance tool to accompany 'Process Cooling Virtual INPLT Training' delivered by the US DOE. US DOE, ORNL, C2A Sustainable Solutions makes no warranty, express or implied, or assumes any legal liability or responsibility for the accuracy or completeness of any information provided or recommended. This tool should be used as a general guidance only.
Acknowledgments:
The developers of CWST would like to acknowledge the efforts of Subodh Chaudhari (Oak Ridge National Laboratory) and Hudson Technologies Company in helping to develop this tool. Additionally, the funding for this tool in its final form was provided by the Industrial Energy Efficiency UNIDO Project (National Cleaner Production Center - South Africa).
Copy Right Notice:
CWST is protected under copy right law. It is the property of C2A Sustainable Solutions, LLC, USA. This tool or no part of this tool may be directly or indirectly reproduced, copied, sold, or exchanged to external parties without prior consent from C2A Sustainable Solutions, LLC. All Rights Reserved.

## Background Information
Basic Facility Information |  |  |  |  | Industry | Process Cooling | Comfort Cooling | Comfort Cooling | Process Cooling | Category | Generic Potential
Contact Information |  |  |  |  | Agro-Processing | H | L | L | H | H | > 40%
Company Name: | DuPont |  | Location: | St. Louis, MO | Chemicals & Liquid Fuels | H | L | L | H | M | between 10% and 40%
Plant/Facility Name: | St. Louis, MO Plant |  | Primary Contact Person: | John Doe | Mining | L | H | H | H | L | < 10%
Address: | 1234 Main Street, St. Louis, MO |  | Industry Sector: | Chemicals & Liquid Fuels | Automotives | H | L | L | H
Phone: |  |  | Application: | Process Cooling | Metals & Fabrication | L | L | L | H
Fax: |  |  | Specify if other: |  | Non-metallic Minerals | M | L | L | M
Email: |  |  | Primary Product: | Fruit products | Food & Beverage | H | L | L | H
[5 empty] | Pulp & Paper | L | L | L | M
Operation Hours |  |  |  |  | Textiles & Leather | M | L | L | M
Shift No. | Hours of Operation / Day | Days/Week | Weeks/Year | Annual Hours | Commercial Buildings | L | H | H | L
1 | 8 | 7 | 52 | 2912 | Data Centers | H | L | L | H
2 | 8 | 7 | 52 | 2912 | Tourism & Hospitality | L | H | H | L
3 | 8 | 7 | 52 | 2912 | Medical Centers/Hospitals | L | H | H | M
Office Hours |  |  |  | 0
Others |  |  |  | 0
Specific Pre-Identified Problems: | 1.
2.
3.
Energy Efficiency Ideas of Interest to Plant Personnel: | 1.
2.
3.
Energy Use: | Based on the industry, the major application selected accounts for > 40% of the annual plant energy spend
Note on H5: Select the industry type from the drop down list.
Note on G6: If there multiple applications, include the one that uses most energy.
Note on H6: Select the application for cooling. Large scale cooling includes comfort cooling as well as process cooling plants
Note on B24: Select Industry Type and Major Application to see generic potential for energy use savings.

## Chilled Water System
Chilled Water System Scorecard
Sr. | Question | Answer | Score | Multiplier |  | Sr | Option | Option Score Weight
Chilled Water Plant
| General |  | 46 |  | 90
1 | How old is the chilled water plant system (equipment)? | 10- 20 years | 5 |  |  | 1 | <10 Years | 10
[6 empty] | 2 | 10- 20 years | 5
[6 empty] | 3 | >20 Years | 0
2 | When was the last time the chilled water system was audited? | >5 years ago or Never | 0 |  |  | 1 | 1 year or less | 10
[6 empty] | 2 | >2 years ago | 5
[6 empty] | 3 | >5 years ago or Never | 0
3 | Is the chilled water system operating energy cost monitored? How often? | Yes, annually | 5 |  |  | 1 | Yes, monthly or more frequently | 10
[6 empty] | 2 | Yes, Quarterly/Seasonally | 6
[6 empty] | 3 | Yes, annually | 5
[6 empty] | 4 | No | 0
4 | How is the chilled water plant controlled? | DCS / BMS | 5 |  |  | 1 | DCS / BMS & state of the art optimization package | 10
[6 empty] | 2 | DCS / BMS | 5
[6 empty] | 3 | Manual Control | 0
5 | Has a detailed chilled water system load analysis ever done to minimize the cooling done? | Don't know | 5 |  |  | 1 | Yes | 10
[6 empty] | 2 | No | 0
[6 empty] | 3 | Don't know | 5
6 | What percent of the chilled water plant capacity is generally utilized versus design? | Higher than 50% | 5 |  |  | 1 | Close to design or higher (>=80%) | 10
[6 empty] | 2 | Higher than 50% | 5
[6 empty] | 3 | Lower than 50% | 0
7 | Is there a regular maintenance program? | Yes | 10 |  |  | 1 | Yes | 10
[6 empty] | 2 | No | 0
8 | How is the overall quality of insulation of the chilled water system? | Good but can be improved | 5 |  |  | 1 | Very Good | 10
[6 empty] | 2 | Good but can be improved | 5
[6 empty] | 3 | Needs significant improvement | 0
9 | Is the refrigerant charge level in each chiller inspected regularly? How often? | Yes, Quarterly | 6 |  |  | 1 | Yes, monthly or more frequently | 10
[6 empty] | 2 | Yes, Quarterly | 6
[6 empty] | 3 | Yes, annually | 5
[6 empty] | 4 | No | 0
System Components
1 | Choose main components for the chilled water system
| Compressors | Yes | 1 |  |  |  | Yes | 1
| Condensers (Water-Cooled or Air-Cooled) | Yes | 1 |  |  |  | No | 0
| Evaporators | Yes | 1
| Cooling Towers | Yes | 1
| Water Side Economizers/Plate Heat Exchangers | No | 0
| Pumps | Yes | 1
| Compressors |  | 53 | 1 | 80
1 | Is inspection and regular maintenance conducted on the compressors? | Yes, as needed only | 5 |  |  | 1 | Yes, as per manufacturers recommendations | 10
[6 empty] | 2 | Yes, as needed only | 5
[6 empty] | 3 | No | 0
2 | What is the average running compressor load factor versus design? | Higher than 50% | 5 |  |  | 1 | Close to design or higher (>=80%) | 10
[6 empty] | 2 | Higher than 50% | 5
[6 empty] | 3 | Lower than 50% | 0
3 | What percent of operating time is spent at less than 50% load? | 30% or less | 10 |  |  | 1 | 30% or less | 10
[6 empty] | 2 | 60% or less | 5
[6 empty] | 3 | All the time | 0
4 | Is compressor efficiency monitored? How often? | No | 0 |  |  | 1 | Yes, monthly or more frequently | 10
[6 empty] | 2 | Yes, Quarterly | 6
[6 empty] | 3 | Yes, annually | 5
[6 empty] | 4 | No | 0
5 | Select the most common control mechanism for the compressors | Variable inlet guide vanes (centrifugal) | 8 |  |  | 1 | Variable speed drives | 10
[6 empty] | 2 | Cylinder unloading (reciprocating) | 8
[6 empty] | 3 | Slide valves (screw) | 8
[6 empty] | 4 | Variable inlet guide vanes (centrifugal) | 8
[6 empty] | 5 | Automatic on/off | 6
[6 empty] | 6 | Manual on/off | 3
[6 empty] | 7 | Suction throttling | 2
[6 empty] | 8 | Hot gas bypass | 0
6 | Is the operating suction pressure lower than the design suction pressure by more than 15%? | No | 10 |  |  | 1 | No | 10
[6 empty] | 2 | Yes | 0
7 | Is the operating discharge pressure higher than the design discharge pressure by more than 10%? | No | 10 |  |  | 1 | No | 10
[6 empty] | 2 | Yes | 0
8 | What percent of the compressor power is delivered via the following drive types? (Total must be less than or equal to 100%) |  | 5 |  |  | 1 |  | 10
| Backpressure (extraction ) steam turbines | 0% |  |  |  | (i) | Backpressure (extraction ) steam turbines | 10
| Variable Speed Electric Motor | 0% |  |  |  | (ii) | Variable Speed Electric Motor | 10
| Electric motor with constant speed | 100% |  |  |  | (iii) | Electric motor w/o variable speed drives | 5
| Condensing steam turbines | 0% |  |  |  | (iv) | Condensing steam turbines | 0
| Total | 100%
| Condensers |  | 35 | 1 | 75
1 | What is the most common heat rejection methodology in the chilled water system? | Cooling Towers | 10 |  |  | 1 | Cooling Towers | 10
[6 empty] | 2 | Air Cooled Condensers | 0
2 | Is inspection and regular maintenance conducted on the condensers? | Yes, as needed only | 5 |  |  | 1 | Yes, as per manufacturers recommendations | 10
[6 empty] | 2 | Yes, as needed only | 5
[6 empty] | 3 | No | 0
4
3 | Are there any condenser issues such as fouling, non-condensables, etc.? | Yes, sometimes | 5 |  |  | 1 | No | 10
[6 empty] | 2 | Yes, sometimes | 5
[6 empty] | 3 | Yes, most of the time | 0
4 | Are the following operating parameters monitored continuously:
| (i) Water flow | No | 0 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
| (ii) Water supply & return temperature | Yes | 5 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
| (iii) Refrigerant pressure | No | 0 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
5 | Are the following conditions representative during normal operations:
| (i) Water flow lower than design | Don't Know | 0 |  |  | 1 | No | 10
[6 empty] | 2 | Yes | 0
[6 empty] | 3 | Don't Know | 0
| (ii) Waterside pressure drop (dP) higher than design | Don't Know | 0 |  |  | 1 | No | 10
[6 empty] | 2 | Yes | 0
[6 empty] | 3 | Don't Know | 0
| (iii) Approach temperature higher than design | No | 10 |  |  | 1 | No | 10
[6 empty] | 2 | Yes, slightly higher | 5
[6 empty] | 3 | Yes, higher by 50% or more | 0
| Evaporators |  | 35 | 1 | 70
1 | Is inspection and regular maintenance conducted on the evaporator for fouling? | Yes, as needed only | 5 |  |  | 1 | Yes, as per manufacturers recommendations | 10
[6 empty] | 2 | Yes, as needed only | 5
[6 empty] | 3 | No | 0
2 | Is the chilled water exchanger pressure drop (ΔP) monitored? | No | 0 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
3 | Does the evaporator have any issues such as fouling, high superheat, etc.? | No | 10 |  |  | 1 | No | 10
[6 empty] | 2 | Yes, sometimes | 5
[6 empty] | 3 | Yes, most of the time | 0
4 | Are the following operating parameters monitored continuously:
| (i) Coolant flow | No | 0 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
| (ii) Coolant supply and return temperatures | Yes | 5 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
| (iii) Refrigerant pressure | Yes | 5 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
5 | Are the following conditions representative during normal operations:
| (i) Coolant flow lower than design | Don't Know | 0 |  |  | 1 | No | 10
[6 empty] | 2 | Yes | 0
[6 empty] | 3 | Don't Know | 0
| (ii) Coolant pressure drop (dP) higher than design | Don't Know | 0 |  |  | 1 | No | 10
[6 empty] | 2 | Yes | 0
[6 empty] | 3 | Don't Know | 0
| (iii) Approach temperature higher than design | No | 10 |  |  | 1 | No | 10
[6 empty] | 2 | Yes, slightly higher | 5
[6 empty] | 3 | Yes, higher by 50% or more | 0
| Cooling Towers |  | 33 | 1 | 62
1 | What is general condition of the cooling towers? | Good | 5 |  |  | 1 | Excellent | 10
[6 empty] | 2 | Good | 5
[6 empty] | 3 | In need of replacement | 0
2 | How are your cooling tower fans controlled? | Automated ON/OFF | 4 |  |  | 1 | Variable Speed Drives | 5
[6 empty] | 2 | Automated ON/OFF | 4
[6 empty] | 3 | Fan blade pitch control | 4
[6 empty] | 4 | Manual on/off control | 2
[6 empty] | 5 | Always on | 0
3 | How is your cooling tower water blowdown controlled? | Manual | 2 |  |  | 1 | Automatic | 5
[6 empty] | 2 | Manual | 2
[6 empty] | 3 | Combination | 0
4 | Do you monitor the following operating parameters continuously?
| (i) Cooling tower water flow | No | 0 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
| (ii) Water outlet temperature | Yes | 5 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
| (iii) Water Inlet Temperature | No | 0 |  |  | 1 | Yes | 2
[6 empty] | 2 | No | 0
| (iv) Ambient air wet bulb temperature | No | 0 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
| (v) Ambient air temperature | Yes | 2 |  |  | 1 | Yes | 2
[6 empty] | 2 | No | 0
| (vi) Cooling tower water chemistry | No | 0 |  |  | 1 | Yes | 3
[6 empty] | 2 | No | 0
5 | Are your overall cooling water flow rates lower than design? | No | 5 |  |  | 1 | No | 5
[6 empty] | 2 | Yes, slightly lower | 2
[6 empty] | 3 | Yes, lower by 25% or more | 0
4
6 | Do you see an evenly spread and uniform water distribution in your cooling towers? | Yes | 5 |  |  | 1 | Yes | 5
[6 empty] | 2 | No | 0
7 | How close is the approach of supply cooling water temperature to the wet bulb temperature? | 10°F to 20°F | 5 |  |  | 1 | Within 4 to 10°F | 10
[6 empty] | 2 | 10°F to 20°F | 5
[6 empty] | 3 | Higher than 20°F | 0
[6 empty] | 2 | Yes | 0
[6 empty] | 3 | Don't know | 2
| Plate Heat Exchangers/Waterside Economizers |  | 23 | 0 | 23
1 | Do you observe fouling on cooling tower water heat exchangers? | No | 5 |  |  | 1 | No | 5
[6 empty] | 2 | Yes | 0
2 | Do you monitor cooling water exchanger pressure drop (ΔP)? | Yes | 3 |  |  | 1 | Yes | 3
[6 empty] | 2 | No | 0
3 | Are the following conditions representative during operations:
| (i) Cooling tower water flow and/or coolant flow lower than design | No | 5 |  |  | 1 | No | 5
[6 empty] | 2 | Yes | 0
[6 empty] | 3 | Don't Know | 0
| (ii) Cooling tower water dP and/or coolant dP higher than design dP | No | 5 |  |  | 1 | No | 5
[6 empty] | 2 | Yes | 0
[6 empty] | 3 | Don't Know | 0
| (iii) Approach temperature higher than design | No | 5 |  |  | 1 | No | 5
[6 empty] | 2 | Yes | 0
[6 empty] | 3 | Don't Know | 0
| Pumps |  | 7 | 1 | 20
1 | What percent of cooling water pump power delivered by the following drive types (Total must be less than or equal to 100%) |  | 7
| Backpressure turbine drives | 0% |  |  |  | 1 | Backpressure turbine drives | 10
| Variable speed drives | 25% |  |  |  | 2 | Variable speed drives | 10
| Constant speed motors | 75% |  |  |  | 3 | Motor drives | 6
| Condensing turbine drives | 0% |  |  |  | 4 | Condensing turbine drives | 0
| Total | 100%
2 | Are you only running the minimum number of pumps? | No | 0 |  |  | 1 | Yes | 10
[6 empty] | 2 | No | 0
Note on H89: Enter numeric values in corresponding grey cells
Note on C104: i.e. are you unable to meet design condensing temperature?
Note on C140: Evaporator performance problem is signified by evaporator unable to produce design cooling

## Summary
Chilled Water System Scoping Tool (CWST) Summary
Points Details
| Maximum Score = | 397
| Your Score = | 209
| Best Practices Rating = | 52.64%
Based on plant information, there is medium potential and energy savings in the range of 5-15% can be anticipated.
Section |  |  | Your Score | Maximum Score | %
General |  |  | 46 | 90 | 51.1111
System Components
Compressors |  |  | 53 | 80 | 66.25
Condensers |  |  | 35 | 75 | 46.6667
Evaporators |  |  | 35 | 70 | 50
Cooling Towers |  |  | 33 | 62 | 53.2258
Plate Heat Exchangers/Waterside Economizers |  |  | 0 | 0 | 0
Pumps |  |  | 7 | 20 | 35
Total |  |  | 209 | 397 | 52.6448

## Info (hidden)
Best Practices Rating
Low | High | Potential | % Savings
0 | 0.4 | high | 10-20%
0.4 | 0.85 | medium | 5-15%
0.85 | 1 | low | 0-10%

## Sheet2 (hidden)
Energy Efficiency Measures
[6 empty] | Question | Score
Equipment | Payback Category | Level | Questions | Sr. | Descriptions
General | Near Term | High | 1,2,3,45,7,8,9 | 1 | Perform a detailed Refrigeration / Process Cooling System Assessment at your site
General | Near Term | High |  | 2 | Use the DOE CWSAT software tool & other resources to identify and quantify energy saving opportunities
Cooling Tower | Near Term | High |  | 3 | Lower condenser water temperature setpoint
Chiller, Evaporator | Near Term | High |  | 4 | Raise chilled water temperature setpoint
General | Near Term | High |  | 5 | Ensure proper refrigerant charge and eliminate non-condensable from the system
Plate Exchanger, Condenser, Cooling Tower | Medium Term | Medium |  | 1 | Use waterside economizer in the system (cooling tower water vs. chilled water)
AHU | Medium Term | Medium |  | 2 | Use airside economizer in the system (cold air intake vs recircuilation)
Compressor | Medium Term | Medium |  | 3 | Sequence refrigeration compressors for optimum system efficiency
Cooling Towers | Medium Term | Medium |  | 4 | Install condenser water temperature reset control
Chiller | Medium Term | Medium |  | 5 | Install chilled water temperature reset control
Chiller | Medium Term | Medium |  | 6 | Incorporate optimized chiller sequencing and controls
Evaporator, Condenser, Heat Exchanger | Medium Term | Medium |  | 7 | Perform maintenace on heat exchanger tubes to improve heat transfer
Cooling Tower, Water Treatment | Medium Term | Medium |  | 8 | Implement a predictive maintenance program that correlates performance with fluid contaminants in the system
General | Long Term | Low |  | 1 | Install continuous commissioning / fault detection and diagnostic system along with comensurate operation and maintenance program
Compressor, Pump, Fan | Long Term | Low |  | 2 | Install variable speed motors (compressors, pumps, fans)
Chiller | Long Term | Low |  | 3 | Evaluate chiller replacement (type, size) for a more efficient overall system or plant efficiency
Chiller | Long Term | Low |  | 4 | Install absorption chiller to make use of available waste heat stream
Chiller | Long Term | Low |  | 5 | Evaluate heat recovery from chiller systems
Chiller | Long Term | Low |  | 6 | Convert air-cooled chillers to water-cooled units
Chiller, Steam | Long Term | Low |  | 7 | Evaluate use of steam driven chiller systems to balance steam and electric demand
Chiller | Long Term | Low |  | 8 | Install instrumentation to measure and trend individual compressor and overall system performance (efficiency - kW/ton) periodically