Process Exhaust Heat Recovery

Case description

A manufacturing facility is considering a heat exchanger that will recover heat from a continuous dryer or oven exhaust and use it to preheat incoming air. The team must determine whether the energy, financial, and emissions benefits justify the investment and implementation risks. All values are hypothetical.

Project data

| Input | Value | Input | Value |
| --- | --- | --- | --- |
| Current natural-gas use | 80,000 MMBtu/year | Equipment cost | $280,000 |
| Expected gas reduction | 20% | Installation cost | $140,000 |
| Additional electricity | 100 MWh/year | Engineering and commissioning | $40,000 |
| Natural-gas price | $6.00/MMBtu | Contingency | $40,000 |
| Electricity price | $80/MWh | Utility incentive | $50,000 |
| Additional maintenance | $12,000/year | Project life | 10 years |
| Annual production | 100,000 units | Discount rate | 8% |
| Natural-gas emissions factor | 0.053 tCO2e/MMBtu | Residual value in year 10 | $20,000 |
| Electricity emissions factor | 0.35 tCO2e/MWh | Project type | Exhaust heat recovery |

Implementation considerations

Consider exhaust condensation and corrosion, added pressure drop, combustion-system effects, hot-surface exposure, maintenance access, fouling, and production downtime during installation.

Before calculating

What additional technical or operating data would you request?

Which input appears most uncertain? Why?

​

Part 1: Cost and Performance

Show the calculation or spreadsheet reference for each result.

Capital and annual savings

| Calculation | Formula or approach | Your result |
| --- | --- | --- |
| Total installed cost | Equipment + installation + engineering + contingency |  |
| Net investment | Total installed cost - incentive |  |
| Natural gas saved | Current gas use × expected reduction |  |
| Gross fuel-cost savings | Natural gas saved × gas price |  |
| Added electricity cost | Additional electricity × electricity price |  |
| Net annual savings | Fuel savings - added electricity - added maintenance |  |

Production-cost effect

| Calculation | Formula or approach | Your result |
| --- | --- | --- |
| Baseline energy cost per unit | Current gas cost / annual production |  |
| New operating cost per unit | Remaining gas + added electricity + maintenance, divided by production |  |
| Operating cost reduction per unit | Baseline cost per unit - new operating cost per unit |  |
| Optional annualized cost per unit | Add annualized net investment to the new annual operating cost |  |

Part 2: Financial Evaluation and Uncertainty

Use a calculator or spreadsheet for the discounted cash-flow calculations.

Financial metrics

| Metric | Formula or cash-flow setup | Your result |
| --- | --- | --- |
| Annual simple ROI | Net annual savings / net investment |  |
| Simple payback | Net investment / net annual savings |  |
| Net present value | Year 0 investment; years 1-9 savings; year 10 savings + residual value |  |
| Internal rate of return | IRR of the annual project cash-flow series |  |

Break-even questions

1. What natural-gas price gives the project a five-year simple payback?

2. What percentage gas reduction gives an NPV of zero at the base gas price?

Scenario analysis

| Scenario | Gas price | Gas reduction | Net investment | Annual savings | NPV |
| --- | --- | --- | --- | --- | --- |
| Downside | $4/MMBtu | 15% | $550,000 |  |  |
| Base | $6/MMBtu | 20% | $450,000 |  |  |
| Upside | $8/MMBtu | 20% | $450,000 |  |  |
| Scenario | Parameter 1 | Parameter 2 | Net investment | Annual savings | NPV |
| Downside (alternative) |  |  |  |  |  |
| Baseline (alternative) |  |  |  |  |  |
| Upside (alternative) |  |  |  |  |  |

Which assumption has the strongest effect on the recommendation?

What should the project team measure during a pilot or commissioning period?

Part 3: EHS, Strategic Fit, and Recommendation

Use the financial results together with operating and sustainability considerations.

EHS and implementation review

| Issue | Risk or consequence | Proposed control | Data needed |
| --- | --- | --- | --- |
| Condensation and corrosion |  |  |  |
| Pressure drop and combustion stability |  |  |  |
| Hot surfaces and maintenance access |  |  |  |
| Fouling and cleaning |  |  |  |
| Installation and production downtime |  |  |  |

Strategic scorecard

| Criterion | Weight | Rating, 1-5 | Evidence for rating |
| --- | --- | --- | --- |
| Financial return | 30% |  |  |
| Energy reduction | 25% |  |  |
| Implementation and EHS risk | 20% |  |  |
| Operational fit | 15% |  |  |
| Replication at other facilities | 10% |  |  |

Weighted score: ____________________ / 5.0

Final recommendation

☐ Approve      ☐ Reject      ☐ Conditional approval

State the decision and cite the calculations that support it. Add any approval conditions.